## test_file
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level
287.0211 | 283.5728 | 302.7232 | 305.9926 | 283.15 | 0.013574 | 0.01687 | NoF | 0 | 57.5337 | -196083.8885 | 287.0211 | 283.5728 | 0.0035352 | 0.0032638 | 1.4289e-05 | 1.7738e-05 | 0.090939 | 331.1712 | 0.0081956 | 0.0070162 | 0.012345 | 0.012525 | 6.9955e-07 | -2.4459e-06 | 0.00080527 | 0.1689% | 0.1581% | 3.4082 | 196.0839 | 0
285.1628 | 283.2962 | 302.6607 | 304.5239 | 283.15 | 0.013574 | 0.016943 | NoF | 0 | 42.4033 | -106201.144 | 285.1628 | 283.2962 | 0.0034386 | 0.0042815 | 1.4276e-05 | 1.7799e-05 | 0.068925 | 280.7022 | 0.013549 | 0.019668 | -0.0016335 | -0.01023 | 1.205e-07 | -5.9568e-07 | 0.00085124 | 0.2643% | 0.1625% | 2.5045 | 106.2011 | 0
289.3396 | 283.2563 | 297.3904 | 303.1459 | 282.5944 | 0.013614 | 0.016704 | NoF | 0 | 75.9413 | -346708.8515 | 289.3396 | 283.2563 | 0.0031795 | 0.0034681 | 1.4313e-05 | 1.7548e-05 | 0.11968 | 475.8415 | -0.025143 | -0.031243 | -0.0098445 | -0.005959 | 7.6866e-07 | 1.0574e-06 | 0.00058385 | 0.1372% | 0.1576% | 4.5655 | 346.7089 | 0
284.9085 | 283.3896 | 297.1093 | 298.6959 | 283.15 | 0.013572 | 0.01683 | NoF | 0 | 35.0978 | -86416.0624 | 284.9085 | 283.3896 | 0.004789 | 0.0056103 | 1.4275e-05 | 1.7684e-05 | 0.060402 | 273.6682 | 0.0016149 | 0.00010352 | -0.010847 | -0.01864 | 1.3926e-06 | 1.1925e-06 | -7.1667e-05 | 0.3167% | 0.1721% | 2.4622 | 86.4161 | 0
288.2445 | 283.1384 | 294.5706 | 299.32 | 282.5944 | 0.013593 | 0.016774 | NoF | 0 | 60.5082 | -290664.1768 | 288.2445 | 283.1384 | 0.00301 | 0.0030414 | 1.43e-05 | 1.7618e-05 | 0.095309 | 415.0542 | -0.015969 | -0.015078 | -0.0053639 | -0.0040643 | 3.1229e-07 | 1.6398e-06 | -0.00075872 | 0.1428% | 0.1575% | 4.8037 | 290.6642 | 0
286.4847 | 283.1062 | 291.6634 | 294.7821 | 283.15 | 0.013593 | 0.016907 | NoF | 0 | 42.4875 | -192431.2297 | 286.4847 | 283.1062 | 0.0029399 | 0.0030077 | 1.4289e-05 | 1.7756e-05 | 0.066811 | 326.2953 | -0.00059457 | -0.00031003 | -0.00044381 | -0.0050624 | -2.8793e-06 | 1.6091e-06 | -0.00085332 | 0.1696% | 0.1572% | 4.5291 | 192.4312 | 0
285.116 | 283.2578 | 290.0515 | 291.8041 | 283.15 | 0.013583 | 0.017029 | NoF | 0 | 32.2977 | -105801.7462 | 285.116 | 283.2578 | 0.0030693 | 0.0034222 | 1.428e-05 | 1.7882e-05 | 0.052047 | 275.889 | 0.015505 | 0.018688 | 0.0019594 | -0.0016754 | 2.1981e-06 | 2.1522e-07 | -0.0007377 | 0.2608% | 0.1611% | 3.2758 | 105.8017 | 0
282.5718 | 280.5848 | 302.7032 | 304.748 | 280.3722 | 0.01356 | 0.01697 | NoF | 0 | 45.3258 | -113082.5014 | 282.5718 | 280.5848 | 0.0030708 | 0.0030267 | 1.4278e-05 | 1.7837e-05 | 0.071285 | 270.0064 | -0.011196 | -0.011273 | 0.0055513 | 0.0027987 | 8.3799e-07 | 3.5991e-07 | -0.00054181 | 0.2388% | 0.1573% | 2.4949 | 113.0825 | 0
283.424 | 280.1028 | 297.0002 | 300.2167 | 279.8167 | 0.013563 | 0.016955 | NoF | 0 | 50.1651 | -189036.5873 | 283.424 | 280.1028 | 0.0031662 | 0.0036226 | 1.4246e-05 | 1.7818e-05 | 0.07939 | 325.088 | 0.025763 | 0.025722 | -0.0016154 | -0.0083946 | -1.125e-06 | -3.3278e-07 | 3.5356e-05 | 0.172% | 0.1583% | 3.7683 | 189.0366 | 0
282.0679 | 280.4712 | 297.0236 | 298.6849 | 280.3722 | 0.013555 | 0.017002 | NoF | 0 | 36.4886 | -90854.8306 | 282.0679 | 280.4712 | 0.0033401 | 0.0037958 | 1.4269e-05 | 1.7864e-05 | 0.058472 | 261.7815 | 0.02559 | 0.024439 | -6.105e-05 | -0.0033079 | 1.8526e-06 | -3.4448e-06 | 0.00029623 | 0.2881% | 0.1602% | 2.49 | 90.8548 | 0
283.6647 | 279.9495 | 291.1873 | 294.6703 | 279.8167 | 0.013578 | 0.017005 | NoF | 0 | 46.0997 | -211691.896 | 283.6647 | 279.9495 | 0.0029944 | 0.0031951 | 1.4281e-05 | 1.7858e-05 | 0.072495 | 342.5026 | 0.0031406 | 0.0011456 | -0.0040219 | -0.010766 | -1.0641e-06 | 1.556e-06 | 0.0006173 | 0.1618% | 0.1573% | 4.592 | 211.6919 | 0
282.1998 | 280.3885 | 291.2821 | 293.0744 | 280.3722 | 0.013557 | 0.017057 | NoF | 0 | 33.7887 | -103072.0916 | 282.1998 | 280.3885 | 0.0032564 | 0.0034241 | 1.4262e-05 | 1.7917e-05 | 0.053163 | 266.1458 | -0.021899 | -0.022902 | 0.0087609 | 0.0098407 | -2.3078e-06 | -3.707e-06 | 0.00025991 | 0.2582% | 0.1573% | 3.0505 | 103.0721 | 0
279.8512 | 277.9211 | 299.8631 | 301.9245 | 277.5944 | 0.013545 | 0.017051 | NoF | 0 | 43.3151 | -109896.1367 | 279.8512 | 277.9211 | 0.0029964 | 0.0030435 | 1.4245e-05 | 1.7906e-05 | 0.068135 | 270.4159 | -0.021765 | -0.025724 | 0.0038509 | 0.005296 | 3.9126e-06 | 1.2763e-06 | 0.00041089 | 0.2461% | 0.1573% | 2.5371 | 109.8961 | 0
280.7859 | 277.2556 | 293.87 | 297.2818 | 277.0389 | 0.013558 | 0.017025 | NoF | 0 | 49.3107 | -201167.6907 | 280.7859 | 277.2556 | 0.0036778 | 0.0041998 | 1.4275e-05 | 1.7888e-05 | 0.078141 | 338.8024 | -0.0010931 | 0.0032426 | -0.0075909 | -0.010919 | 5.4138e-07 | -1.1563e-06 | 0.00058098 | 0.1684% | 0.1585% | 4.0796 | 201.1677 | 0
279.3957 | 277.6217 | 293.9101 | 295.7896 | 277.5944 | 0.013537 | 0.017081 | NoF | 0 | 36.4974 | -100962.6349 | 279.3957 | 277.6217 | 0.004125 | 0.0043694 | 1.424e-05 | 1.794e-05 | 0.05801 | 266.0068 | -0.0036588 | -0.0028651 | -0.023256 | -0.026536 | -1.2835e-06 | 9.3625e-07 | -0.00068323 | 0.2635% | 0.1589% | 2.7663 | 100.9626 | 0
281.4628 | 277.6535 | 291.4612 | 295.0916 | 277.5944 | 0.013564 | 0.016931 | NoF | 0 | 48.3152 | -217081.5734 | 281.4628 | 277.6535 | 0.003127 | 0.00345 | 1.427e-05 | 1.7783e-05 | 0.076244 | 348.7011 | 0.011977 | 0.015733 | -0.0045294 | -0.010016 | 1.0062e-06 | 6.5532e-07 | 0.00019016 | 0.1606% | 0.1578% | 4.493 | 217.0816 | 0
279.6371 | 277.6245 | 291.5059 | 293.5774 | 277.5944 | 0.013555 | 0.016975 | NoF | 0 | 36.2696 | -114683.9759 | 279.6371 | 277.6245 | 0.002923 | 0.0029245 | 1.4265e-05 | 1.7835e-05 | 0.057034 | 271.2941 | -0.003026 | -0.0019748 | -0.00080055 | -0.0011631 | -2.1155e-06 | 1.4523e-06 | -0.00092403 | 0.2366% | 0.1572% | 3.162 | 114.684 | 0
284.6953 | 283.151 | 297.5871 | 299.1621 | 283.15 | 0.013572 | 0.016828 | NoF | 0 | 35.3175 | -87867.6288 | 284.6953 | 283.151 | 0.0030794 | 0.0033672 | 1.4263e-05 | 1.7681e-05 | 0.055818 | 259.8245 | 0.0098959 | 0.01211 | -0.0043738 | -0.010199 | 1.7146e-06 | 4.1779e-07 | -0.00038318 | 0.2957% | 0.158% | 2.4879 | 87.8676 | 0
286.6256 | 283.0832 | 292.2171 | 295.5073 | 283.15 | 0.013598 | 0.016848 | NoF | 0 | 43.9168 | -201837.4757 | 286.6256 | 283.0832 | 0.0029654 | 0.0033459 | 1.4322e-05 | 1.77e-05 | 0.06928 | 338.8019 | 0.003251 | 0.007661 | -0.0017243 | -0.010618 | -3.2597e-06 | -1.0707e-06 | 0.0003182 | 0.1679% | 0.1578% | 4.5959 | 201.8375 | 0
282.4686 | 280.5144 | 302.8174 | 304.8356 | 280.3234 | 0.013565 | 0.016992 | NoF | 0 | 44.989 | -111261.6813 | 282.4686 | 280.5144 | 0.0061578 | 0.0056137 | 1.428e-05 | 1.7845e-05 | 0.075225 | 282.6551 | 0.024223 | 0.022248 | -0.039547 | -0.038558 | 2.7376e-06 | -8.8622e-08 | 0.00073865 | 0.254% | 0.1672% | 2.4731 | 111.2617 | 0
284.7487 | 280.8287 | 297.7124 | 301.4658 | 279.8167 | 0.013586 | 0.016909 | NoF | 0 | 55.5002 | -223371.6162 | 284.7487 | 280.8287 | 0.0029411 | 0.0029788 | 1.4292e-05 | 1.7762e-05 | 0.087281 | 353.0318 | -0.01926 | -0.016018 | -0.00048203 | -0.0029474 | 1.5608e-06 | -1.8828e-06 | -0.00063736 | 0.158% | 0.1573% | 4.0247 | 223.3716 | 0
283.5443 | 279.8208 | 292.2771 | 295.7757 | 279.8167 | 0.013592 | 0.017201 | NoF | 0 | 47.0492 | -212395.5369 | 283.5443 | 279.8208 | 0.003069 | 0.0035592 | 1.4311e-05 | 1.8082e-05 | 0.074292 | 346.387 | 0.0074662 | 0.0096921 | -0.0030525 | -0.0099182 | -2.2451e-06 | 6.8848e-07 | -0.00012613 | 0.1631% | 0.1579% | 4.5143 | 212.3955 | 0
282.3742 | 280.4748 | 292.3634 | 294.2605 | 280.3722 | 0.013574 | 0.016947 | NoF | 0 | 34.6895 | -108218.0277 | 282.3742 | 280.4748 | 0.0036097 | 0.0045909 | 1.4272e-05 | 1.78e-05 | 0.056792 | 281.7857 | 0.012665 | 0.015665 | -0.0052137 | -0.007549 | -3.6956e-07 | -4.2743e-07 | 0.00079121 | 0.2604% | 0.1637% | 3.1196 | 108.218 | 0
281.5702 | 278.2284 | 300.3774 | 303.6549 | 277.5944 | 0.013563 | 0.016973 | NoF | 0 | 56.3491 | -190400.1062 | 281.5702 | 278.2284 | 0.002931 | 0.0029343 | 1.4273e-05 | 1.7832e-05 | 0.088651 | 325.2088 | 0.0034655 | 0.0063639 | -0.00061066 | -0.0012452 | -4.3137e-09 | -1.0134e-06 | -0.00050855 | 0.1708% | 0.1573% | 3.3789 | 190.4001 | 0
279.9294 | 278.002 | 300.1488 | 302.2274 | 277.5944 | 0.013551 | 0.01703 | NoF | 0 | 43.097 | -109778.8685 | 279.9294 | 278.002 | 0.006892 | 0.009437 | 1.424e-05 | 1.7891e-05 | 0.080623 | 305.6336 | 0.026622 | 0.037354 | 0.0029405 | -0.012323 | -1.2431e-06 | -1.6826e-06 | -0.00046632 | 0.2784% | 0.1871% | 2.5472 | 109.7789 | 0
280.867 | 277.3397 | 294.2999 | 297.6792 | 277.0389 | 0.013557 | 0.016985 | NoF | 0 | 49.1535 | -200966.6688 | 280.867 | 277.3397 | 0.0037738 | 0.0043456 | 1.4245e-05 | 1.7848e-05 | 0.078065 | 341.7091 | 0.024273 | 0.029359 | -0.0018538 | -0.0073265 | 2.6587e-07 | 3.9186e-08 | 0.0008753 | 0.17% | 0.1588% | 4.0886 | 200.9667 | 0
281.5033 | 277.8125 | 291.4421 | 294.9814 | 277.5944 | 0.013561 | 0.016902 | NoF | 0 | 46.5063 | -210266.4282 | 281.5033 | 277.8125 | 0.0041833 | 0.0069492 | 1.4269e-05 | 1.775e-05 | 0.076879 | 422.2507 | -0.019298 | -0.0004562 | -0.012952 | -0.028925 | 4.7237e-07 | 5.4675e-06 | -0.0005212 | 0.2008% | 0.1653% | 4.5212 | 210.2664 | 0
279.5734 | 277.6569 | 291.2495 | 293.2273 | 277.5944 | 0.013548 | 0.01696 | NoF | 0 | 34.9742 | -109153.595 | 279.5734 | 277.6569 | 0.0029118 | 0.0029205 | 1.4171e-05 | 1.7715e-05 | 0.054702 | 266.242 | -0.021602 | -0.021518 | -0.0015053 | -0.0026889 | 1.1826e-06 | -3.9136e-06 | 0.00076985 | 0.2439% | 0.1564% | 3.121 | 109.1536 | 0
289.4975 | 283.9184 | 303.1569 | 308.4018 | 282.625 | 0.013616 | 0.016838 | UC | 10 | 83.3485 | -317967.5902 | 289.4975 | 283.9184 | 0.0039671 | 0.0037398 | 1.4322e-05 | 1.7695e-05 | 0.13672 | 445.1566 | -0.0047274 | -0.0063556 | 0.01599 | 0.018799 | -1.2118e-07 | -2.2258e-06 | -0.00040612 | 0.14% | 0.164% | 3.8149 | 317.9676 | -10
285.2089 | 283.3288 | 302.9882 | 304.8701 | 283.15 | 0.013595 | 0.01704 | UC | 10 | 43.1821 | -107136.5349 | 285.2089 | 283.3288 | 0.0031586 | 0.0032765 | 1.4297e-05 | 1.7894e-05 | 0.068641 | 269.5138 | -0.027852 | -0.030164 | -0.0065713 | -0.0046784 | 1.5854e-06 | -1.8472e-06 | 0.0009102 | 0.2516% | 0.159% | 2.481 | 107.1365 | -10
288.9947 | 283.2889 | 297.3038 | 302.665 | 282.5944 | 0.013627 | 0.016787 | UC | 10 | 70.8889 | -325543.3168 | 288.9947 | 283.2889 | 0.0032194 | 0.0033331 | 1.434e-05 | 1.7637e-05 | 0.11166 | 451.5501 | -0.024157 | -0.026683 | -0.011075 | -0.0094415 | 5.972e-08 | 1.6929e-06 | 0.0006926 | 0.1387% | 0.1575% | 4.5923 | 325.5433 | -10
286.8985 | 283.2828 | 297.5716 | 300.9607 | 283.15 | 0.013603 | 0.0169 | UC | 10 | 51.4691 | -206059.9088 | 286.8985 | 283.2828 | 0.002988 | 0.0030083 | 1.4314e-05 | 1.7759e-05 | 0.080946 | 338.7134 | -0.021158 | -0.019527 | -0.00065191 | -0.0016436 | -7.5781e-07 | -1.3426e-06 | 0.00086765 | 0.1644% | 0.1573% | 4.0036 | 206.0599 | -10
284.8264 | 283.2868 | 297.4267 | 298.9828 | 283.15 | 0.013587 | 0.016899 | UC | 10 | 35.3724 | -87691.0759 | 284.8264 | 283.2868 | 0.0035057 | 0.0038687 | 1.4292e-05 | 1.7776e-05 | 0.057261 | 267.207 | 0.026127 | 0.028302 | 0.0050783 | 0.0044859 | -1.6808e-06 | -7.5913e-06 | 0.00025323 | 0.3047% | 0.1619% | 2.4791 | 87.6911 | -10
286.5147 | 283.1143 | 291.783 | 294.9455 | 283.15 | 0.01362 | 0.016956 | UC | 10 | 42.8795 | -194059.4391 | 286.5147 | 283.1143 | 0.0030944 | 0.0032147 | 1.4317e-05 | 1.7808e-05 | 0.067759 | 331.453 | -0.014477 | -0.01847 | -0.0065488 | -0.010947 | -1.899e-06 | -6.5713e-08 | 0.0002322 | 0.1708% | 0.158% | 4.5257 | 194.0594 | -10
285.1974 | 283.1156 | 290.7062 | 292.6385 | 283.15 | 0.013606 | 0.017084 | UC | 10 | 34.0088 | -118729.4647 | 285.1974 | 283.1156 | 0.003342 | 0.0040682 | 1.4305e-05 | 1.7946e-05 | 0.05364 | 280.5376 | 0.0060307 | 0.010062 | -0.0087694 | -0.017064 | -1.717e-06 | -1.8749e-07 | 0.00028189 | 0.2363% | 0.1577% | 3.4911 | 118.7295 | -10
283.9981 | 280.522 | 303.1947 | 306.5783 | 280.3722 | 0.013603 | 0.016995 | UC | 10 | 61.4275 | -198371.3254 | 283.9981 | 280.522 | 0.0029459 | 0.0029508 | 1.4297e-05 | 1.7866e-05 | 0.096627 | 331.3027 | -0.017292 | -0.016975 | -0.0010363 | -0.0021744 | 1.6277e-07 | -1.3504e-06 | -0.00075394 | 0.167% | 0.1573% | 3.2294 | 198.3713 | -10
282.4005 | 280.3766 | 303.0301 | 305.1209 | 280.3722 | 0.013589 | 0.017071 | UC | 10 | 46.2127 | -115438.4903 | 282.4005 | 280.3766 | 0.0039338 | 0.0048828 | 1.4286e-05 | 1.7931e-05 | 0.074707 | 280.3336 | -0.01607 | -0.010394 | 0.0011987 | -0.0043521 | 1.2299e-07 | 5.4439e-07 | 0.0001806 | 0.2428% | 0.1617% | 2.498 | 115.4385 | -10
282.2467 | 280.6029 | 297.3809 | 299.0628 | 280.3539 | 0.013602 | 0.017048 | UC | 10 | 37.0049 | -93852.0524 | 282.2467 | 280.6029 | 0.0030063 | 0.0029568 | 1.4302e-05 | 1.7909e-05 | 0.058394 | 260.2749 | 0.00082603 | 0.00046133 | -0.0064899 | -0.0045464 | 2.0154e-06 | -8.2111e-07 | 0.00058098 | 0.2773% | 0.1578% | 2.5362 | 93.8521 | -10
281.1733 | 277.3523 | 295.0471 | 298.6892 | 277.0389 | 0.013562 | 0.01706 | UC | 10 | 52.791 | -217754.7791 | 281.1733 | 277.3523 | 0.0029377 | 0.0029377 | 1.4262e-05 | 1.7931e-05 | 0.083019 | 347.6568 | -0.00073897 | -0.0011127 | 0.002287 | 0.0025885 | -8.5004e-08 | 1.3468e-06 | -0.00049594 | 0.1597% | 0.1573% | 4.1248 | 217.7548 | -10
279.5859 | 277.5354 | 292.0719 | 294.1836 | 277.5944 | 0.013575 | 0.01704 | UC | 10 | 36.3995 | -117023.5435 | 279.5859 | 277.5354 | 0.0029325 | 0.0029359 | 1.4286e-05 | 1.79e-05 | 0.057242 | 272.6495 | 0.00041886 | 0.00011254 | -0.001074 | -0.002149 | 1.269e-06 | -2.4211e-06 | -0.00097563 | 0.233% | 0.1573% | 3.215 | 117.0235 | -10
289.4874 | 283.792 | 303.3427 | 308.7384 | 282.5944 | 0.013612 | 0.016817 | UC | 20 | 85.1125 | -324502.4336 | 289.4874 | 283.792 | 0.0029202 | 0.0030017 | 1.4324e-05 | 1.7666e-05 | 0.13394 | 448.9747 | -0.0027775 | -0.0033158 | 0.00019961 | 0.0023247 | 1.925e-06 | -1.3384e-07 | 0.00034018 | 0.1384% | 0.1574% | 3.8126 | 324.5024 | -20
285.0077 | 283.1159 | 303.1122 | 305.0083 | 283.15 | 0.013579 | 0.017007 | UC | 20 | 43.2727 | -107681.0161 | 285.0077 | 283.1159 | 0.0029448 | 0.0029518 | 1.4367e-05 | 1.7964e-05 | 0.068426 | 268.5414 | -0.002635 | -0.0021449 | -1.0294e-05 | -0.00098898 | 7.0632e-07 | 9.3217e-08 | -0.00028063 | 0.2494% | 0.1581% | 2.4884 | 107.681 | -20
286.838 | 283.1972 | 297.7759 | 301.2312 | 283.15 | 0.013597 | 0.016827 | UC | 20 | 51.7273 | -207410.8772 | 286.838 | 283.1972 | 0.0029632 | 0.0029555 | 1.4378e-05 | 1.7791e-05 | 0.081797 | 340.823 | -0.00040712 | -0.00024306 | -0.00015811 | 0.0002093 | 1.5172e-06 | -7.3377e-06 | 0.00079125 | 0.1643% | 0.1581% | 4.0097 | 207.4109 | -20
284.3436 | 280.8416 | 303.2966 | 306.6873 | 280.3722 | 0.013578 | 0.016955 | UC | 20 | 61.2355 | -199460.1589 | 284.3436 | 280.8416 | 0.0029732 | 0.0030286 | 1.4294e-05 | 1.7829e-05 | 0.096425 | 332.6248 | -0.029103 | -0.028444 | 0.0019175 | 0.003517 | 1.3528e-06 | -2.1553e-06 | 0.00081414 | 0.1668% | 0.1575% | 3.2573 | 199.4602 | -20
282.2209 | 280.5353 | 297.4835 | 299.1611 | 280.3722 | 0.013574 | 0.017038 | UC | 20 | 37.2756 | -96045.1982 | 282.2209 | 280.5353 | 0.0030596 | 0.0030584 | 1.428e-05 | 1.791e-05 | 0.058617 | 261.4417 | -0.0039014 | -0.0045204 | 0.0056182 | 0.0053087 | -3.9126e-07 | 5.7996e-07 | 0.00069661 | 0.2722% | 0.1573% | 2.5766 | 96.0452 | -20
282.5093 | 280.5132 | 292.3178 | 294.3062 | 280.3722 | 0.01357 | 0.017076 | UC | 20 | 35.6096 | -113690.8423 | 282.5093 | 280.5132 | 0.0031067 | 0.0031998 | 1.4272e-05 | 1.793e-05 | 0.056534 | 280.7794 | -0.031785 | -0.03639 | -0.0062446 | -0.00448 | 3.4002e-07 | -2.5911e-06 | -0.00045772 | 0.247% | 0.1588% | 3.1927 | 113.6908 | -20
281.2636 | 277.8284 | 300.124 | 303.4798 | 277.6555 | 0.013538 | 0.017018 | UC | 20 | 56.0434 | -195400.0188 | 281.2636 | 277.8284 | 0.003099 | 0.0035771 | 1.424e-05 | 1.7879e-05 | 0.088448 | 336.3175 | 0.039469 | 0.049479 | -0.0032192 | -0.012953 | 9.6519e-07 | 4.0995e-08 | 0.00049116 | 0.1721% | 0.1578% | 3.4866 | 195.4 | -20
279.5754 | 277.6342 | 299.9596 | 302.0367 | 277.57 | 0.013547 | 0.017077 | UC | 20 | 43.0141 | -110552.9572 | 279.5754 | 277.6342 | 0.0031684 | 0.0031363 | 1.4245e-05 | 1.7927e-05 | 0.068094 | 269.5956 | 0.013738 | 0.015047 | -0.0058656 | -0.0064596 | 4.2563e-07 | -6.2276e-07 | 0.0009441 | 0.2439% | 0.1583% | 2.5702 | 110.553 | -20
282.9006 | 277.6438 | 291.5501 | 296.4499 | 277.0389 | 0.013574 | 0.016943 | UC | 20 | 59.9766 | -299658.5827 | 282.9006 | 277.6438 | 0.0029435 | 0.0030139 | 1.4268e-05 | 1.7799e-05 | 0.094462 | 423.6553 | 0.0072379 | 0.0079461 | -0.0017965 | -0.0047311 | 1.1732e-06 | 8.8803e-07 | -0.00069565 | 0.1414% | 0.1575% | 4.9963 | 299.6586 | -20
279.8114 | 277.8497 | 291.4498 | 293.4643 | 277.5944 | 0.013531 | 0.017073 | UC | 20 | 35.1645 | -111572.7044 | 279.8114 | 277.8497 | 0.0061149 | 0.0071365 | 1.4229e-05 | 1.794e-05 | 0.061295 | 299.049 | -0.01208 | -0.010128 | -0.031004 | -0.039433 | 2.1788e-06 | 6.3482e-07 | -0.00089823 | 0.268% | 0.1743% | 3.1729 | 111.5727 | -20
289.3771 | 283.552 | 303.3591 | 308.8915 | 282.5944 | 0.01362 | 0.016793 | UC | 30 | 85.5597 | -332135.0311 | 289.3771 | 283.552 | 0.0029264 | 0.002938 | 1.4333e-05 | 1.7634e-05 | 0.13459 | 456.0677 | 0.0017609 | 0.0017508 | 0.00031215 | 0.001703 | -1.3305e-06 | -1.975e-06 | -0.00027234 | 0.1373% | 0.1573% | 3.8819 | 332.135 | -30
284.9557 | 283.3742 | 297.6389 | 299.2231 | 283.15 | 0.013587 | 0.016809 | UC | 30 | 35.5711 | -90067.999 | 284.9557 | 283.3742 | 0.0029499 | 0.0029525 | 1.4284e-05 | 1.7651e-05 | 0.05601 | 258.519 | -0.011306 | -0.010738 | 0.001925 | -8.8821e-05 | -1.0864e-06 | -2.1875e-06 | 0.00085109 | 0.287% | 0.1575% | 2.5321 | 90.068 | -30
282.5399 | 280.5899 | 302.9217 | 304.9293 | 280.3722 | 0.013568 | 0.017006 | UC | 30 | 44.6968 | -111044.4834 | 282.5399 | 280.5899 | 0.002934 | 0.0029285 | 1.4263e-05 | 1.7879e-05 | 0.070287 | 269.2501 | -0.014614 | -0.015231 | -0.0024048 | -0.0019079 | -1.3824e-06 | 1.6639e-07 | 0.00050741 | 0.2425% | 0.1573% | 2.4844 | 111.0445 | -30
281.2294 | 277.7677 | 300.3964 | 303.8275 | 277.5944 | 0.013566 | 0.016982 | UC | 30 | 57.1186 | -197314.282 | 281.2294 | 277.7677 | 0.0030131 | 0.0030475 | 1.4265e-05 | 1.7851e-05 | 0.089879 | 331.0645 | 0.00062483 | -0.00041249 | 0.0044354 | 0.0026443 | -9.9413e-07 | 4.1206e-06 | 0.0009441 | 0.1678% | 0.1574% | 3.4545 | 197.3143 | -30
281.1606 | 277.4255 | 294.981 | 298.5871 | 277.0389 | 0.013574 | 0.016986 | UC | 30 | 51.3509 | -213044.2521 | 281.1606 | 277.4255 | 0.0029555 | 0.0029874 | 1.4274e-05 | 1.7837e-05 | 0.080757 | 343.5984 | -0.0030015 | -0.0026432 | 0.00054096 | -0.0034862 | 4.3768e-07 | 3.6413e-07 | -0.0009957 | 0.1613% | 0.1573% | 4.1488 | 213.0443 | -30
279.7222 | 277.8673 | 295.0071 | 296.939 | 277.5944 | 0.013546 | 0.01704 | UC | 30 | 37.4424 | -105614.1448 | 279.7222 | 277.8673 | 0.0029514 | 0.0029576 | 1.4242e-05 | 1.7899e-05 | 0.058887 | 266.3324 | 0.021956 | 0.019415 | 0.0029877 | 0.00094707 | -8.3377e-07 | 1.1653e-06 | -0.00097754 | 0.2522% | 0.1573% | 2.8207 | 105.6141 | -30
281.5671 | 277.5616 | 292.1773 | 296.0103 | 277.5944 | 0.013574 | 0.016919 | UC | 30 | 49.7695 | -228429.67 | 281.5671 | 277.5616 | 0.0029405 | 0.0029755 | 1.4275e-05 | 1.7756e-05 | 0.078308 | 357.6166 | 0.011067 | 0.011279 | 0.0015735 | -0.001513 | 1.8924e-06 | -6.2216e-07 | -0.00017391 | 0.1566% | 0.1573% | 4.5898 | 228.4297 | -30
279.6179 | 277.6065 | 292.0755 | 294.1519 | 277.5944 | 0.013542 | 0.016966 | UC | 30 | 36.0541 | -114513.3607 | 279.6179 | 277.6065 | 0.0029536 | 0.0029849 | 1.4253e-05 | 1.7827e-05 | 0.056707 | 271.4291 | 0.010701 | 0.011783 | -0.00058873 | -0.0021235 | 1.266e-06 | 8.1206e-07 | 0.00026374 | 0.237% | 0.1573% | 3.1762 | 114.5134 | -30
287.0883 | 283.4784 | 302.8436 | 306.254 | 283.15 | 0.013587 | 0.016931 | UC | 40 | 57.4503 | -205464.7408 | 287.0883 | 283.4784 | 0.0032676 | 0.0036133 | 1.4285e-05 | 1.7782e-05 | 0.098744 | 344.7977 | 0.041556 | 0.028439 | 0.01471 | 0.021876 | -9.5121e-07 | -2.2224e-06 | -6.5637e-05 | 0.1678% | 0.1719% | 3.5764 | 205.4647 | -40
289.4085 | 283.125 | 297.596 | 303.524 | 282.5944 | 0.013588 | 0.016682 | UC | 40 | 75.6907 | -357440.4936 | 289.4085 | 283.125 | 0.0029737 | 0.0029712 | 1.4296e-05 | 1.7552e-05 | 0.1191 | 481.3988 | -0.014014 | -0.014458 | -0.0036545 | -0.0036742 | -9.2842e-07 | -1.3691e-06 | -0.00088772 | 0.1347% | 0.1573% | 4.7224 | 357.4405 | -40
284.8435 | 283.3159 | 297.3253 | 298.8894 | 283.15 | 0.013563 | 0.01682 | UC | 40 | 35.1136 | -86848.7673 | 284.8435 | 283.3159 | 0.0042609 | 0.0046885 | 1.4279e-05 | 1.7676e-05 | 0.055313 | 263.6288 | -0.016939 | -0.021163 | 0.021374 | 0.023327 | 1.6621e-06 | -1.644e-06 | -0.00085905 | 0.3035% | 0.1575% | 2.4734 | 86.8488 | -40
288.0078 | 283.0616 | 294.2924 | 298.8733 | 282.5944 | 0.013584 | 0.016771 | UC | 40 | 56.5103 | -281403.4151 | 288.0078 | 283.0616 | 0.0029691 | 0.0029765 | 1.4286e-05 | 1.7617e-05 | 0.088907 | 405.7547 | -0.0037665 | -0.0051898 | -0.0036832 | -0.0042661 | 1.0219e-06 | -2.0299e-06 | -0.00097946 | 0.1442% | 0.1573% | 4.9797 | 281.4034 | -40
286.4908 | 283.0524 | 291.7523 | 294.9455 | 283.15 | 0.013589 | 0.01688 | UC | 40 | 41.9916 | -195786.3919 | 286.4908 | 283.0524 | 0.0030838 | 0.0033904 | 1.4286e-05 | 1.7726e-05 | 0.066034 | 329.4685 | -0.00099591 | -0.00058077 | -0.0055009 | -0.012651 | -2.11e-06 | 4.9918e-07 | 3.5356e-05 | 0.1683% | 0.1573% | 4.6625 | 195.7864 | -40
285.0855 | 283.0706 | 290.423 | 292.3132 | 283.15 | 0.013566 | 0.017025 | UC | 40 | 33.0531 | -114583.6926 | 285.0855 | 283.0706 | 0.0031855 | 0.0036967 | 1.4271e-05 | 1.7876e-05 | 0.052189 | 275.9481 | -0.005391 | -0.003069 | -0.0073462 | -0.014459 | -2.145e-06 | 5.9081e-08 | 3.7267e-05 | 0.2408% | 0.1579% | 3.4667 | 114.5837 | -40
286.0982 | 280.7049 | 302.9389 | 308.1098 | 279.8167 | 0.013584 | 0.016865 | UC | 40 | 82.2244 | -307144.1862 | 286.0982 | 280.7049 | 0.0029649 | 0.0029309 | 1.4281e-05 | 1.7733e-05 | 0.12933 | 430.7538 | -0.013643 | -0.01209 | -0.0049955 | -0.00067314 | 5.2872e-07 | 1.6862e-06 | 0.00090301 | 0.1402% | 0.1573% | 3.7354 | 307.1442 | -40
282.0287 | 280.4216 | 297.1529 | 298.8325 | 280.3661 | 0.01356 | 0.016975 | UC | 40 | 36.4 | -91484.7828 | 282.0287 | 280.4216 | 0.0029412 | 0.0029274 | 1.4262e-05 | 1.7843e-05 | 0.057238 | 258.4278 | -0.0031067 | -0.0025402 | 0.0026974 | 0.0010978 | -1.0984e-06 | -1.1617e-06 | 0.00095939 | 0.2825% | 0.1572% | 2.5133 | 91.4848 | -40
282.2777 | 280.3715 | 291.6616 | 293.5318 | 280.3722 | 0.013558 | 0.017037 | UC | 40 | 34.0742 | -108485.7629 | 282.2777 | 280.3715 | 0.0030508 | 0.003087 | 1.4256e-05 | 1.7898e-05 | 0.053595 | 267.8507 | -0.019382 | -0.020384 | 0.0012698 | 0.00047778 | 1.2497e-06 | -2.23e-06 | 0.00088581 | 0.2469% | 0.1573% | 3.1838 | 108.4858 | -40
279.862 | 277.9173 | 299.7605 | 301.8288 | 277.5944 | 0.01354 | 0.017054 | UC | 40 | 42.5715 | -110673.6512 | 279.862 | 277.9173 | 0.0029832 | 0.0029843 | 1.4244e-05 | 1.7923e-05 | 0.06695 | 268.4886 | -0.0029453 | -0.0036651 | 0.0033254 | 0.0014854 | -1.2823e-06 | 1.3667e-06 | 0.00048925 | 0.2426% | 0.1573% | 2.5997 | 110.6737 | -40
283.1305 | 278.0023 | 291.4993 | 296.3242 | 277.0389 | 0.013567 | 0.016932 | UC | 40 | 59.5341 | -292130.0771 | 283.1305 | 278.0023 | 0.0029305 | 0.0029345 | 1.4252e-05 | 1.7783e-05 | 0.093659 | 415.8724 | 0.0042101 | 0.0030924 | 0.00050355 | 0.0013375 | -7.061e-07 | -9.0428e-07 | -0.00088883 | 0.1424% | 0.1573% | 4.9069 | 292.1301 | -40
281.6242 | 277.8814 | 291.5716 | 295.1457 | 277.5944 | 0.013546 | 0.016909 | UC | 40 | 46.9936 | -212990.6466 | 281.6242 | 277.8814 | 0.0029176 | 0.0029337 | 1.4172e-05 | 1.7666e-05 | 0.073495 | 341.4087 | 0.0011131 | 0.0003797 | -0.00039944 | -0.0019629 | -1.5247e-06 | -1.1939e-06 | -0.00086317 | 0.1603% | 0.1564% | 4.5323 | 212.9906 | -40
279.687 | 277.7567 | 291.2959 | 293.2949 | 277.5944 | 0.013525 | 0.01693 | UC | 40 | 34.8418 | -109747.6319 | 279.687 | 277.7567 | 0.0029573 | 0.0029532 | 1.414e-05 | 1.7694e-05 | 0.054525 | 266.833 | -0.019614 | -0.018022 | 0.00035859 | -0.0017806 | -3.203e-07 | -1.9218e-06 | -0.00025569 | 0.2431% | 0.1565% | 3.1499 | 109.7476 | -40
286.7684 | 283.2836 | 302.6867 | 306.027 | 283.15 | 0.013584 | 0.016911 | UC | 40 | 56.4979 | -198324.6977 | 286.7684 | 283.2836 | 0.0030884 | 0.0034673 | 1.4291e-05 | 1.7765e-05 | 0.089347 | 332.5462 | 0.01999 | 0.01975 | -0.00075065 | -0.0061719 | -1.9732e-06 | 9.9654e-07 | 0.00026756 | 0.1677% | 0.1581% | 3.5103 | 198.3247 | -40
289.257 | 283.0788 | 297.3394 | 303.1819 | 282.5944 | 0.01361 | 0.016668 | UC | 40 | 73.6295 | -352030.8682 | 289.257 | 283.0788 | 0.0030033 | 0.0030827 | 1.4313e-05 | 1.7522e-05 | 0.11588 | 477.2945 | -0.016168 | -0.019154 | -0.0053581 | -0.0012491 | 1.761e-06 | 2.0069e-06 | 0.00063927 | 0.1356% | 0.1574% | 4.7811 | 352.0309 | -40
284.806 | 283.4539 | 296.579 | 298.062 | 283.15 | 0.013574 | 0.016901 | UC | 40 | 33.2834 | -76933.0569 | 284.806 | 283.4539 | 0.0084512 | 0.010904 | 1.4282e-05 | 1.7777e-05 | 0.14342 | 543.245 | 0.0015326 | 0.0054478 | -0.0062043 | -0.013301 | -1.3474e-06 | 1.6416e-06 | 0.0001376 | 0.7061% | 0.4309% | 2.3115 | 76.9331 | -40
288.0303 | 282.9596 | 294.3938 | 299.1232 | 282.5944 | 0.013599 | 0.016738 | UC | 40 | 57.9058 | -288810.4361 | 288.0303 | 282.9596 | 0.0029647 | 0.0029623 | 1.4299e-05 | 1.7599e-05 | 0.091143 | 414.4741 | -0.012848 | -0.016957 | -0.0049689 | -0.0041089 | 8.2472e-07 | 1.2057e-08 | 0.00013569 | 0.1435% | 0.1574% | 4.9876 | 288.8104 | -40
286.5016 | 283.0361 | 291.7007 | 294.9016 | 283.15 | 0.013584 | 0.016864 | UC | 40 | 42.0475 | -197260.8494 | 286.5016 | 283.0361 | 0.0029507 | 0.0032335 | 1.4289e-05 | 1.7729e-05 | 0.066589 | 334.9751 | -0.0037623 | -0.0043717 | -0.0025482 | -0.0078818 | 1.0785e-06 | -1.4825e-06 | -0.00075776 | 0.1698% | 0.1584% | 4.6914 | 197.2608 | -40
285.0871 | 283.2582 | 290.073 | 291.8291 | 283.15 | 0.013582 | 0.017015 | UC | 40 | 31.8916 | -104124.7492 | 285.0871 | 283.2582 | 0.0035537 | 0.0046587 | 1.4296e-05 | 1.7875e-05 | 0.059229 | 322.7355 | -0.0097027 | -0.012368 | 0.00090301 | -0.00066146 | 2.154e-06 | 1.5554e-07 | 5.3512e-05 | 0.31% | 0.1857% | 3.265 | 104.1247 | -40
283.9963 | 280.6111 | 302.7775 | 306.0954 | 280.3722 | 0.013577 | 0.016929 | UC | 40 | 57.9724 | -192822.8822 | 283.9963 | 280.6111 | 0.0029365 | 0.0029903 | 1.4275e-05 | 1.78e-05 | 0.091186 | 326.8138 | -0.0061682 | -0.0077735 | 0.00059033 | -3.5568e-05 | 1.5554e-06 | 1.7978e-06 | 0.00019111 | 0.1695% | 0.1573% | 3.3261 | 192.8229 | -40
286.493 | 280.4507 | 297.1641 | 302.8997 | 279.8167 | 0.013603 | 0.016829 | UC | 40 | 75.8831 | -344570.059 | 286.493 | 280.4507 | 0.002968 | 0.0030058 | 1.4297e-05 | 1.77e-05 | 0.12213 | 468.5656 | -0.00026544 | -0.0038053 | 0.0027462 | 0.0070165 | -7.4635e-07 | -1.2618e-06 | -0.00058672 | 0.136% | 0.161% | 4.5408 | 344.5701 | -40
283.2962 | 279.9882 | 297.0792 | 300.3437 | 279.8533 | 0.013574 | 0.016932 | UC | 40 | 49.0105 | -188443.9568 | 283.2962 | 279.9882 | 0.0045797 | 0.0063652 | 1.4273e-05 | 1.7794e-05 | 0.081773 | 353.9356 | -0.014234 | -0.00084992 | -0.013256 | -0.029527 | 5.0762e-07 | -1.0671e-07 | -0.00070712 | 0.1878% | 0.1668% | 3.845 | 188.444 | -40
282.0087 | 280.3651 | 297.0781 | 298.8205 | 280.3722 | 0.013558 | 0.016962 | UC | 40 | 36.6484 | -93549.1739 | 282.0087 | 280.3651 | 0.0034181 | 0.0038541 | 1.425e-05 | 1.783e-05 | 0.058585 | 263.2592 | -0.0097696 | -0.0065228 | -0.0062202 | -0.010205 | 2.7491e-07 | -2.6189e-06 | 8.5045e-05 | 0.2814% | 0.1599% | 2.5526 | 93.5492 | -40
286.1744 | 280.2874 | 294.3926 | 299.9419 | 279.8167 | 0.013587 | 0.016822 | UC | 40 | 68.7009 | -335375.9096 | 286.1744 | 280.2874 | 0.0030247 | 0.0031463 | 1.4282e-05 | 1.7679e-05 | 0.10821 | 459.5377 | -0.0078818 | -0.0086691 | -0.0048798 | -0.0061491 | -7.4876e-07 | 2.0763e-06 | 0.00087721 | 0.137% | 0.1575% | 4.8817 | 335.3759 | -40
281.3151 | 277.9432 | 299.7866 | 303.1328 | 277.5944 | 0.013569 | 0.016999 | UC | 40 | 56.3311 | -192229.7127 | 281.3151 | 277.9432 | 0.0029221 | 0.0029325 | 1.4269e-05 | 1.7864e-05 | 0.088882 | 326.0589 | 0.0036651 | 0.0034676 | 0.0015926 | 0.002253 | -3.6896e-07 | 1.6561e-06 | 0.00011467 | 0.1696% | 0.1578% | 3.4125 | 192.2297 | -40
279.5245 | 277.5505 | 299.7649 | 301.8674 | 277.6555 | 0.013534 | 0.017052 | UC | 40 | 43.2324 | -112313.672 | 279.5245 | 277.5505 | 0.0029308 | 0.0029311 | 1.4224e-05 | 1.7921e-05 | 0.067982 | 269.3199 | -0.001969 | -0.0015523 | 0.0020343 | 0.0012762 | -1.2226e-06 | -2.5501e-07 | -0.00082465 | 0.2398% | 0.1572% | 2.5979 | 112.3137 | -40
280.8937 | 277.3933 | 293.8264 | 297.2435 | 277.0389 | 0.013556 | 0.017027 | UC | 40 | 49.4981 | -199407.2776 | 280.8937 | 277.3933 | 0.0030032 | 0.0031587 | 1.425e-05 | 1.7876e-05 | 0.077839 | 332.0327 | -0.0016712 | -0.00069863 | -0.002442 | -0.0084716 | 1.5669e-06 | -6.9089e-07 | -0.00086765 | 0.1665% | 0.1573% | 4.0286 | 199.4073 | -40
279.6319 | 278.0214 | 293.0977 | 294.8396 | 277.5944 | 0.013554 | 0.017079 | UC | 40 | 34.747 | -91770.0216 | 279.6319 | 278.0214 | 0.0081943 | 0.010572 | 1.4247e-05 | 1.794e-05 | 0.15183 | 539.7179 | -0.0015746 | 0.0056734 | -0.019141 | -0.027105 | -1.7718e-06 | -1.6157e-07 | -0.00094028 | 0.5881% | 0.4369% | 2.6411 | 91.77 | -40
282.7151 | 277.7847 | 290.7239 | 295.3523 | 277.0389 | 0.013575 | 0.016943 | UC | 40 | 57.2205 | -281075.4835 | 282.7151 | 277.7847 | 0.0029848 | 0.002988 | 1.4287e-05 | 1.7802e-05 | 0.090021 | 405.6507 | 0.0086808 | 0.0090195 | -0.0041429 | -0.0033593 | 1.6591e-06 | 2.2909e-06 | 0.00057716 | 0.1443% | 0.1573% | 4.9121 | 281.0755 | -40
280.9172 | 277.5601 | 289.7252 | 292.9335 | 277.5944 | 0.013562 | 0.016954 | UC | 40 | 42.44 | -191331.4235 | 280.9172 | 277.5601 | 0.0030458 | 0.0031297 | 1.4257e-05 | 1.7808e-05 | 0.066773 | 325.833 | 0.015484 | 0.013411 | -0.00092424 | -0.0024877 | -1.1762e-06 | -1.4975e-06 | -0.00099188 | 0.1703% | 0.1573% | 4.5083 | 191.3314 | -40
279.4461 | 277.8225 | 289.2549 | 290.9529 | 277.5944 | 0.01355 | 0.016975 | UC | 40 | 31.4876 | -92482.9389 | 279.4461 | 277.8225 | 0.0037899 | 0.0034074 | 1.4242e-05 | 1.7831e-05 | 0.049561 | 261.294 | -0.0079986 | -0.0073281 | -0.011129 | -0.0079657 | -9.037e-07 | -9.6881e-07 | -0.00037649 | 0.2825% | 0.1574% | 2.9371 | 92.4829 | -40
286.8916 | 283.4214 | 297.6888 | 301.0009 | 283.15 | 0.013596 | 0.016886 | OC | 10 | 50.8607 | -197667.2088 | 286.8916 | 283.4214 | 0.0034499 | 0.0049931 | 1.4304e-05 | 1.7743e-05 | 0.084335 | 354.5762 | 0.0079116 | 0.012575 | 0.0040983 | -0.0043972 | 2.3259e-06 | 6.2578e-07 | -0.00091161 | 0.1794% | 0.1658% | 3.8864 | 197.6672 | 10
284.6546 | 283.0837 | 297.6448 | 299.2488 | 283.15 | 0.013599 | 0.016866 | OC | 10 | 36.1904 | -89564.3403 | 284.6546 | 283.0837 | 0.0029582 | 0.0029453 | 1.4307e-05 | 1.7721e-05 | 0.05691 | 257.6423 | -0.001805 | -0.0028455 | 0.0039199 | 0.0025312 | -3.622e-06 | -3.1952e-07 | -0.00078165 | 0.2877% | 0.1573% | 2.4748 | 89.5643 | 10
287.9697 | 282.7974 | 294.8574 | 299.7073 | 282.5944 | 0.013618 | 0.016795 | OC | 10 | 62.3167 | -295030.5551 | 287.9697 | 282.7974 | 0.0030223 | 0.0030941 | 1.4316e-05 | 1.765e-05 | 0.098033 | 419.247 | 0.0096656 | 0.0087694 | 0.00044805 | -0.002391 | -2.7672e-07 | -6.6135e-07 | -0.00066316 | 0.1421% | 0.1573% | 4.7344 | 295.0306 | 10
286.6266 | 283.0395 | 292.2103 | 295.5561 | 283.15 | 0.013619 | 0.016923 | OC | 10 | 45.139 | -204687.7739 | 286.6266 | 283.0395 | 0.0029479 | 0.0031119 | 1.4325e-05 | 1.7776e-05 | 0.070995 | 338.0078 | 0.0011573 | 0.0053294 | -0.0006604 | -0.0068461 | -9.887e-08 | 1.1177e-06 | 0.00043574 | 0.1651% | 0.1573% | 4.5346 | 204.6878 | 10
283.8472 | 280.4259 | 303.1304 | 306.4787 | 279.8167 | 0.01359 | 0.016975 | OC | 10 | 61.6515 | -195078.2154 | 283.8472 | 280.4259 | 0.0029861 | 0.0030052 | 1.4289e-05 | 1.7831e-05 | 0.097124 | 329.0349 | -0.029197 | -0.030353 | -0.0035563 | -0.0013739 | -1.5807e-06 | 3.059e-06 | -0.00029336 | 0.1687% | 0.1575% | 3.1642 | 195.0782 | 10
282.2661 | 280.6237 | 297.4568 | 299.131 | 280.3722 | 0.01358 | 0.017012 | OC | 10 | 37.2785 | -93623.7558 | 282.2661 | 280.6237 | 0.0031292 | 0.0030743 | 1.4286e-05 | 1.787e-05 | 0.058647 | 261.4165 | -0.00019483 | -0.0025604 | 0.0072188 | 0.004446 | 1.31e-06 | -1.7935e-06 | -5.0645e-05 | 0.2792% | 0.1573% | 2.5115 | 93.6238 | 10
279.5814 | 277.7703 | 294.915 | 296.8045 | 277.5944 | 0.013561 | 0.017045 | OC | 10 | 37.739 | -103243.6493 | 279.5814 | 277.7703 | 0.0030634 | 0.0031173 | 1.426e-05 | 1.7909e-05 | 0.059358 | 264.9237 | -0.0083941 | -0.0094389 | 0.0057552 | 0.0066847 | -7.0536e-07 | 2.0287e-06 | -0.00020258 | 0.2566% | 0.1573% | 2.7357 | 103.2436 | 10
279.5077 | 277.5353 | 291.4566 | 293.4967 | 277.5944 | 0.01357 | 0.016988 | OC | 10 | 36.0199 | -112517.272 | 279.5077 | 277.5353 | 0.0069757 | 0.0057502 | 1.4269e-05 | 1.7842e-05 | 0.056963 | 280.0333 | 0.010205 | 0.0059542 | -0.032011 | -0.024954 | -1.2636e-06 | -9.9534e-07 | 0.00075012 | 0.2489% | 0.1581% | 3.1238 | 112.5173 | 10
285.2272 | 283.3627 | 302.8593 | 304.7632 | 283.15 | 0.013576 | 0.016973 | OC | 20 | 43.0881 | -106093.6893 | 285.2272 | 283.3627 | 0.0029748 | 0.0029867 | 1.4362e-05 | 1.793e-05 | 0.068417 | 269.4304 | -0.022218 | -0.026069 | -0.00062674 | -0.00014784 | -1.4691e-07 | 1.1835e-06 | 0.00027271 | 0.254% | 0.1588% | 2.4622 | 106.0937 | 20
286.9051 | 283.3443 | 297.5481 | 300.9521 | 283.15 | 0.013591 | 0.016753 | OC | 20 | 51.4985 | -202746.5487 | 286.9051 | 283.3443 | 0.0029699 | 0.0029732 | 1.4298e-05 | 1.7596e-05 | 0.080996 | 335.0016 | -0.0085237 | -0.0084833 | 0.0011 | -0.00023995 | -7.6625e-07 | 1.5705e-06 | 0.00053416 | 0.1652% | 0.1573% | 3.9369 | 202.7465 | 20
286.6576 | 283.0949 | 292.1981 | 295.5438 | 283.15 | 0.013593 | 0.016858 | OC | 20 | 44.9203 | -202917.9708 | 286.6576 | 283.0949 | 0.003154 | 0.0040342 | 1.4302e-05 | 1.7707e-05 | 0.07111 | 342.7452 | -0.002073 | 0.0017391 | -0.0061512 | -0.016621 | -2.0877e-06 | 2.8305e-06 | 0.00098041 | 0.1689% | 0.1583% | 4.5173 | 202.918 | 20
285.1634 | 282.9825 | 291.0973 | 293.1554 | 283.0401 | 0.013597 | 0.017028 | OC | 20 | 35.2411 | -124305.7378 | 285.1634 | 282.9825 | 0.0032478 | 0.0035428 | 1.4297e-05 | 1.7944e-05 | 0.05618 | 279.6703 | -0.0033381 | 0.0019233 | -0.012789 | -0.017274 | 2.0606e-06 | 4.8899e-06 | -0.00060774 | 0.225% | 0.1594% | 3.5273 | 124.3057 | 20
282.6134 | 280.691 | 302.8193 | 304.8194 | 280.3722 | 0.013577 | 0.017 | OC | 20 | 45.0149 | -109535.7623 | 282.6134 | 280.691 | 0.0046421 | 0.0061542 | 1.4285e-05 | 1.7862e-05 | 0.07747 | 290.2711 | 0.01226 | 0.015965 | -0.010587 | -0.014173 | 2.1625e-06 | 2.2125e-07 | -4.0134e-05 | 0.265% | 0.1721% | 2.4333 | 109.5358 | 20
283.4671 | 279.7971 | 291.912 | 295.3345 | 279.8167 | 0.013587 | 0.017226 | OC | 20 | 46.7643 | -209267.2428 | 283.4671 | 279.7971 | 0.004085 | 0.0059488 | 1.4282e-05 | 1.8094e-05 | 0.07365 | 351.8269 | -0.0016064 | 0.0045814 | -0.015218 | -0.031801 | -9.3143e-07 | -9.9172e-07 | 0.00051027 | 0.1681% | 0.1575% | 4.4749 | 209.2672 | 20
282.2289 | 280.3655 | 291.8173 | 293.6766 | 280.3722 | 0.013569 | 0.016977 | OC | 20 | 34.5686 | -106136.1342 | 282.2289 | 280.3655 | 0.0030529 | 0.0031761 | 1.4265e-05 | 1.7832e-05 | 0.054832 | 268.8015 | 0.0018681 | 0.0036641 | -0.00032595 | -0.0003026 | 1.2021e-06 | 9.3987e-07 | 0.00023794 | 0.2533% | 0.1586% | 3.0703 | 106.1361 | 20
281.524 | 278.1705 | 300.1274 | 303.4502 | 277.6555 | 0.013559 | 0.016983 | OC | 20 | 57.4398 | -191010.0537 | 281.524 | 278.1705 | 0.002931 | 0.0029404 | 1.4271e-05 | 1.7841e-05 | 0.090375 | 325.182 | -0.012466 | -0.012747 | -3.3976e-05 | 0.00072411 | -4.4353e-06 | -3.3158e-08 | -0.00050741 | 0.1702% | 0.1573% | 3.3254 | 191.0101 | 20
280.7051 | 277.1949 | 294.0845 | 297.5159 | 277.0389 | 0.013547 | 0.016996 | OC | 20 | 50.4241 | -199859.2206 | 280.7051 | 277.1949 | 0.0029628 | 0.0029849 | 1.4238e-05 | 1.785e-05 | 0.079321 | 332.5297 | 0.0081558 | 0.0099379 | -0.00047354 | -0.0034337 | -7.8674e-07 | 1.7061e-06 | -0.00063258 | 0.1664% | 0.1573% | 3.9636 | 199.8592 | 20
279.4198 | 277.6593 | 294.0994 | 295.9679 | 277.5944 | 0.013543 | 0.017047 | OC | 20 | 36.6698 | -100235.1316 | 279.4198 | 277.6593 | 0.0030258 | 0.0030399 | 1.4243e-05 | 1.7916e-05 | 0.057736 | 262.9852 | 0.0058141 | 0.0057069 | 8.9186e-05 | -0.0029458 | 1.2311e-06 | 1.6428e-06 | 0.00096894 | 0.2624% | 0.1574% | 2.7335 | 100.2351 | 20
281.56 | 277.9241 | 291.3726 | 294.8777 | 277.5944 | 0.01357 | 0.01691 | OC | 20 | 47.4501 | -207277.7753 | 281.56 | 277.9241 | 0.00308 | 0.0031615 | 1.4262e-05 | 1.7785e-05 | 0.074729 | 339.9183 | -0.0069204 | -0.0097797 | -0.0010171 | -0.00031162 | 1.3577e-06 | 1.0014e-06 | -0.00055327 | 0.164% | 0.1575% | 4.3683 | 207.2778 | 20
279.7784 | 277.8261 | 291.7462 | 293.7739 | 277.5944 | 0.013537 | 0.016943 | OC | 20 | 36.2916 | -111088.3421 | 279.7784 | 277.8261 | 0.0030525 | 0.0030947 | 1.4236e-05 | 1.7792e-05 | 0.057117 | 270.3166 | -0.026472 | -0.02737 | 0.0039996 | 0.0022297 | -1.6886e-06 | -1.7302e-07 | -0.00058194 | 0.2433% | 0.1574% | 3.061 | 111.0883 | 20
287.0063 | 283.5676 | 302.7763 | 306.3588 | 282.5944 | 0.013594 | 0.016993 | OC | 30 | 61.9598 | -195822.6862 | 287.0063 | 283.5676 | 0.0029377 | 0.0030431 | 1.4305e-05 | 1.7853e-05 | 0.097481 | 329.3083 | 0.0046067 | 0.0044801 | 0.0024163 | 0.0021858 | -4.1547e-07 | -1.2552e-06 | -0.00044083 | 0.1682% | 0.1573% | 3.1605 | 195.8227 | 30
286.8141 | 283.4049 | 297.3981 | 300.8627 | 283.15 | 0.013592 | 0.016821 | OC | 30 | 52.0383 | -194122.6591 | 286.8141 | 283.4049 | 0.0029815 | 0.0030347 | 1.439e-05 | 1.7782e-05 | 0.082286 | 329.7383 | -0.011536 | -0.010582 | -7.6508e-05 | 0.0017278 | -3.2855e-07 | -8.0064e-06 | 0.00070824 | 0.1699% | 0.1581% | 3.7304 | 194.1227 | 30
284.654 | 283.106 | 297.3562 | 299.0484 | 283.15 | 0.013585 | 0.016846 | OC | 30 | 36.3382 | -88157.3459 | 284.654 | 283.106 | 0.0032701 | 0.0031329 | 1.4293e-05 | 1.769e-05 | 0.057156 | 258.6258 | -0.017804 | -0.020605 | 0.012463 | 0.0085125 | -2.8648e-06 | 1.4776e-06 | -0.00032776 | 0.2934% | 0.1573% | 2.426 | 88.1573 | 30
286.5993 | 283.1772 | 291.8946 | 295.2602 | 283.15 | 0.013587 | 0.016904 | OC | 30 | 44.6202 | -194822.5313 | 286.5993 | 283.1772 | 0.0033668 | 0.0045046 | 1.4293e-05 | 1.7767e-05 | 0.070895 | 340.6042 | 0.0056968 | 0.012091 | -0.0038483 | -0.017778 | -1.5234e-06 | 3.1319e-06 | -3.9178e-05 | 0.1748% | 0.1589% | 4.3662 | 194.8225 | 30
285.1114 | 280.5672 | 300.5208 | 305.04 | 279.8167 | 0.013582 | 0.016984 | OC | 30 | 70.3644 | -258854.2682 | 285.1114 | 280.5672 | 0.0029645 | 0.0031871 | 1.4286e-05 | 1.7846e-05 | 0.1107 | 384.8749 | -0.024183 | -0.026262 | -0.0024139 | 0.0070935 | 8.5065e-07 | -1.3082e-06 | -0.0008151 | 0.1487% | 0.1573% | 3.6788 | 258.8543 | 30
282.2974 | 280.3546 | 292.4126 | 294.4348 | 280.3722 | 0.013562 | 0.016956 | OC | 30 | 35.7657 | -110593.6115 | 282.2974 | 280.3546 | 0.0034132 | 0.0038314 | 1.4264e-05 | 1.7826e-05 | 0.058409 | 278.1971 | -0.011515 | -0.013454 | 0.0013022 | 0.00026862 | -3.1325e-06 | 1.1039e-06 | -0.00014238 | 0.2515% | 0.1633% | 3.0922 | 110.5936 | 30
279.6389 | 277.6612 | 300.3284 | 302.4505 | 277.5944 | 0.013542 | 0.017007 | OC | 30 | 44.8725 | -112582.739 | 279.6389 | 277.6612 | 0.0032208 | 0.0032088 | 1.4244e-05 | 1.7855e-05 | 0.070611 | 270.6654 | -0.014306 | -0.018456 | 0.0058725 | 0.0049928 | -3.9343e-06 | 2.1034e-06 | -0.0001634 | 0.2404% | 0.1574% | 2.5089 | 112.5827 | 30
279.3856 | 277.6435 | 294.2396 | 296.1137 | 277.5944 | 0.013545 | 0.017046 | OC | 30 | 36.7807 | -99206.7712 | 279.3856 | 277.6435 | 0.0035932 | 0.0038077 | 1.424e-05 | 1.7908e-05 | 0.057906 | 263.1722 | -0.015682 | -0.016799 | -0.01677 | -0.02073 | -1.3167e-06 | 2.8058e-06 | -0.00057334 | 0.2653% | 0.1574% | 2.6973 | 99.2068 | 30
282.8115 | 277.9302 | 291.0756 | 295.802 | 277.0389 | 0.013568 | 0.016901 | OC | 30 | 58.7824 | -278127.1992 | 282.8115 | 277.9302 | 0.0032062 | 0.0031153 | 1.4265e-05 | 1.7767e-05 | 0.092635 | 412.4662 | 0.018821 | 0.016783 | -0.012612 | -0.0053719 | 2.2493e-06 | 1.5572e-06 | -0.00043287 | 0.1483% | 0.1576% | 4.7315 | 278.1272 | 30
279.5343 | 277.611 | 291.2667 | 293.28 | 277.5944 | 0.013551 | 0.016951 | OC | 30 | 35.5443 | -109568.755 | 279.5343 | 277.611 | 0.0031724 | 0.0034694 | 1.4255e-05 | 1.7806e-05 | 0.05643 | 271.1525 | -0.0079418 | -0.0083474 | 0.0060392 | 0.0060312 | -1.9967e-06 | 1.3366e-06 | -0.00062781 | 0.2475% | 0.1588% | 3.0826 | 109.5688 | 30
289.5277 | 284.8142 | 302.7595 | 307.6043 | 282.6005 | 0.013598 | 0.016853 | OC | 40 | 78.0202 | -268251.2897 | 289.5277 | 284.8142 | 0.0029348 | 0.0029898 | 1.4301e-05 | 1.7728e-05 | 0.12277 | 393.3409 | -0.0058587 | -0.004833 | -0.0019281 | -0.00031905 | -1.943e-06 | -2.9281e-06 | -0.00065074 | 0.1466% | 0.1574% | 3.4382 | 268.2513 | 40
286.2709 | 282.6626 | 303.1264 | 306.9824 | 282.5944 | 0.013569 | 0.016923 | OC | 40 | 66.2487 | -205180.5265 | 286.2709 | 282.6626 | 0.0029291 | 0.0030159 | 1.4276e-05 | 1.779e-05 | 0.10424 | 336.656 | 0.011004 | 0.0092159 | -0.00047354 | 0.0021235 | -2.1058e-06 | 9.242e-07 | 0.00082083 | 0.1641% | 0.1573% | 3.0971 | 205.1805 | 40
285.4006 | 283.5238 | 303.1318 | 305.2244 | 283.15 | 0.013574 | 0.016975 | OC | 40 | 45.088 | -106773.5475 | 285.4006 | 283.5238 | 0.003368 | 0.0036187 | 1.4353e-05 | 1.7939e-05 | 0.072948 | 272.1195 | -0.023207 | -0.024732 | 0.0045252 | 0.0058863 | -2.1951e-06 | 1.9207e-06 | -0.00088374 | 0.2549% | 0.1618% | 2.3681 | 106.7735 | 40
286.9814 | 283.458 | 297.6877 | 301.4047 | 283.15 | 0.013586 | 0.016832 | OC | 40 | 54.6137 | -200538.2471 | 286.9814 | 283.458 | 0.0029655 | 0.003193 | 1.4298e-05 | 1.7678e-05 | 0.085884 | 333.415 | -0.034163 | -0.032516 | -0.0030111 | -0.0095429 | 3.4364e-07 | -9.3384e-07 | 0.00045772 | 0.1663% | 0.1573% | 3.6719 | 200.5382 | 40
284.691 | 283.1457 | 297.4741 | 299.2214 | 283.15 | 0.013555 | 0.016877 | OC | 40 | 36.5395 | -87817.2559 | 284.691 | 283.1457 | 0.0034953 | 0.0040556 | 1.4268e-05 | 1.7729e-05 | 0.060164 | 270.028 | -0.0057716 | -0.0066773 | 0.0077199 | 0.0076934 | -1.0876e-06 | -2.5574e-06 | -0.00054372 | 0.3075% | 0.1647% | 2.4034 | 87.8173 | 40
286.6121 | 283.1362 | 291.9849 | 295.5484 | 283.15 | 0.013581 | 0.016876 | OC | 40 | 46.7515 | -197800.5322 | 286.6121 | 283.1362 | 0.0029442 | 0.003034 | 1.4271e-05 | 1.7731e-05 | 0.073519 | 330.455 | -0.0026947 | -0.0037755 | -0.0029856 | -0.0065589 | 7.6263e-07 | 1.506e-06 | -0.00096703 | 0.1671% | 0.1573% | 4.2309 | 197.8005 | 40
284.0932 | 280.7379 | 302.8783 | 306.5288 | 279.8167 | 0.013563 | 0.016974 | OC | 40 | 65.6464 | -190914.0394 | 284.0932 | 280.7379 | 0.0029823 | 0.0030648 | 1.4254e-05 | 1.7832e-05 | 0.10325 | 325.4226 | -0.024175 | -0.023221 | 0.00068429 | 0.0024457 | -1.9183e-06 | -1.6452e-06 | 0.00052843 | 0.1705% | 0.1573% | 2.9082 | 190.914 | 40
284.4914 | 280.7979 | 297.5115 | 301.4411 | 279.8167 | 0.013587 | 0.016943 | OC | 40 | 58.1627 | -210487.6718 | 284.4914 | 280.7979 | 0.0031364 | 0.0038696 | 1.4276e-05 | 1.7808e-05 | 0.091509 | 342.9693 | -0.041172 | -0.036511 | -0.0064166 | -0.016688 | -5.0641e-08 | -2.6448e-06 | 0.00092785 | 0.1629% | 0.1573% | 3.6189 | 210.4877 | 40
282.0807 | 280.4472 | 297.4814 | 299.3455 | 280.3722 | 0.013562 | 0.016971 | OC | 40 | 38.4913 | -92996.5628 | 282.0807 | 280.4472 | 0.0029854 | 0.0031358 | 1.4192e-05 | 1.7741e-05 | 0.060472 | 258.0569 | -0.0010028 | -0.0013455 | 0.0037709 | 0.0038253 | -4.5915e-06 | 4.4778e-07 | -1.2022e-05 | 0.2775% | 0.1571% | 2.416 | 92.9966 | 40
279.5588 | 277.5836 | 300.3383 | 302.4651 | 277.5944 | 0.013537 | 0.017018 | OC | 40 | 44.7598 | -112408.473 | 279.5588 | 277.5836 | 0.0029836 | 0.0030669 | 1.4157e-05 | 1.7779e-05 | 0.070177 | 268.405 | 0.0063339 | 0.0067296 | 0.0019141 | -0.00169 | 2.9536e-07 | -1.1499e-06 | 0.00068557 | 0.2388% | 0.1568% | 2.5114 | 112.4085 | 40
281.3109 | 277.7153 | 294.9295 | 298.6486 | 277.0389 | 0.013563 | 0.016995 | OC | 40 | 53.577 | -204896.5795 | 281.3109 | 277.7153 | 0.0029353 | 0.0031045 | 1.4189e-05 | 1.776e-05 | 0.083815 | 334.8614 | -0.00956 | -0.011038 | 0.0015114 | -0.0025104 | -2.371e-06 | -1.4591e-06 | -0.00014703 | 0.1634% | 0.1564% | 3.8243 | 204.8966 | 40

## test_file (graph)
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level
287.0211 | 283.5728 | 302.7232 | 305.9926 | 283.15 | 0.013574 | 0.01687 | NoF | 0 | 57.5337 | -196083.8885 | 287.0211 | 283.5728 | 0.0035352 | 0.0032638 | 1.4289e-05 | 1.7738e-05 | 0.090939 | 331.1712 | 0.0081956 | 0.0070162 | 0.012345 | 0.012525 | 6.9955e-07 | -2.4459e-06 | 0.00080527 | 0.1689% | 0.1581% | 3.4082 | 196.0839 | 0
285.1628 | 283.2962 | 302.6607 | 304.5239 | 283.15 | 0.013574 | 0.016943 | NoF | 0 | 42.4033 | -106201.144 | 285.1628 | 283.2962 | 0.0034386 | 0.0042815 | 1.4276e-05 | 1.7799e-05 | 0.068925 | 280.7022 | 0.013549 | 0.019668 | -0.0016335 | -0.01023 | 1.205e-07 | -5.9568e-07 | 0.00085124 | 0.2643% | 0.1625% | 2.5045 | 106.2011 | 0
289.3396 | 283.2563 | 297.3904 | 303.1459 | 282.5944 | 0.013614 | 0.016704 | NoF | 0 | 75.9413 | -346708.8515 | 289.3396 | 283.2563 | 0.0031795 | 0.0034681 | 1.4313e-05 | 1.7548e-05 | 0.11968 | 475.8415 | -0.025143 | -0.031243 | -0.0098445 | -0.005959 | 7.6866e-07 | 1.0574e-06 | 0.00058385 | 0.1372% | 0.1576% | 4.5655 | 346.7089 | 0
284.9085 | 283.3896 | 297.1093 | 298.6959 | 283.15 | 0.013572 | 0.01683 | NoF | 0 | 35.0978 | -86416.0624 | 284.9085 | 283.3896 | 0.004789 | 0.0056103 | 1.4275e-05 | 1.7684e-05 | 0.060402 | 273.6682 | 0.0016149 | 0.00010352 | -0.010847 | -0.01864 | 1.3926e-06 | 1.1925e-06 | -7.1667e-05 | 0.3167% | 0.1721% | 2.4622 | 86.4161 | 0
288.2445 | 283.1384 | 294.5706 | 299.32 | 282.5944 | 0.013593 | 0.016774 | NoF | 0 | 60.5082 | -290664.1768 | 288.2445 | 283.1384 | 0.00301 | 0.0030414 | 1.43e-05 | 1.7618e-05 | 0.095309 | 415.0542 | -0.015969 | -0.015078 | -0.0053639 | -0.0040643 | 3.1229e-07 | 1.6398e-06 | -0.00075872 | 0.1428% | 0.1575% | 4.8037 | 290.6642 | 0
286.4847 | 283.1062 | 291.6634 | 294.7821 | 283.15 | 0.013593 | 0.016907 | NoF | 0 | 42.4875 | -192431.2297 | 286.4847 | 283.1062 | 0.0029399 | 0.0030077 | 1.4289e-05 | 1.7756e-05 | 0.066811 | 326.2953 | -0.00059457 | -0.00031003 | -0.00044381 | -0.0050624 | -2.8793e-06 | 1.6091e-06 | -0.00085332 | 0.1696% | 0.1572% | 4.5291 | 192.4312 | 0
285.116 | 283.2578 | 290.0515 | 291.8041 | 283.15 | 0.013583 | 0.017029 | NoF | 0 | 32.2977 | -105801.7462 | 285.116 | 283.2578 | 0.0030693 | 0.0034222 | 1.428e-05 | 1.7882e-05 | 0.052047 | 275.889 | 0.015505 | 0.018688 | 0.0019594 | -0.0016754 | 2.1981e-06 | 2.1522e-07 | -0.0007377 | 0.2608% | 0.1611% | 3.2758 | 105.8017 | 0
282.5718 | 280.5848 | 302.7032 | 304.748 | 280.3722 | 0.01356 | 0.01697 | NoF | 0 | 45.3258 | -113082.5014 | 282.5718 | 280.5848 | 0.0030708 | 0.0030267 | 1.4278e-05 | 1.7837e-05 | 0.071285 | 270.0064 | -0.011196 | -0.011273 | 0.0055513 | 0.0027987 | 8.3799e-07 | 3.5991e-07 | -0.00054181 | 0.2388% | 0.1573% | 2.4949 | 113.0825 | 0
283.424 | 280.1028 | 297.0002 | 300.2167 | 279.8167 | 0.013563 | 0.016955 | NoF | 0 | 50.1651 | -189036.5873 | 283.424 | 280.1028 | 0.0031662 | 0.0036226 | 1.4246e-05 | 1.7818e-05 | 0.07939 | 325.088 | 0.025763 | 0.025722 | -0.0016154 | -0.0083946 | -1.125e-06 | -3.3278e-07 | 3.5356e-05 | 0.172% | 0.1583% | 3.7683 | 189.0366 | 0
282.0679 | 280.4712 | 297.0236 | 298.6849 | 280.3722 | 0.013555 | 0.017002 | NoF | 0 | 36.4886 | -90854.8306 | 282.0679 | 280.4712 | 0.0033401 | 0.0037958 | 1.4269e-05 | 1.7864e-05 | 0.058472 | 261.7815 | 0.02559 | 0.024439 | -6.105e-05 | -0.0033079 | 1.8526e-06 | -3.4448e-06 | 0.00029623 | 0.2881% | 0.1602% | 2.49 | 90.8548 | 0
283.6647 | 279.9495 | 291.1873 | 294.6703 | 279.8167 | 0.013578 | 0.017005 | NoF | 0 | 46.0997 | -211691.896 | 283.6647 | 279.9495 | 0.0029944 | 0.0031951 | 1.4281e-05 | 1.7858e-05 | 0.072495 | 342.5026 | 0.0031406 | 0.0011456 | -0.0040219 | -0.010766 | -1.0641e-06 | 1.556e-06 | 0.0006173 | 0.1618% | 0.1573% | 4.592 | 211.6919 | 0
282.1998 | 280.3885 | 291.2821 | 293.0744 | 280.3722 | 0.013557 | 0.017057 | NoF | 0 | 33.7887 | -103072.0916 | 282.1998 | 280.3885 | 0.0032564 | 0.0034241 | 1.4262e-05 | 1.7917e-05 | 0.053163 | 266.1458 | -0.021899 | -0.022902 | 0.0087609 | 0.0098407 | -2.3078e-06 | -3.707e-06 | 0.00025991 | 0.2582% | 0.1573% | 3.0505 | 103.0721 | 0
279.8512 | 277.9211 | 299.8631 | 301.9245 | 277.5944 | 0.013545 | 0.017051 | NoF | 0 | 43.3151 | -109896.1367 | 279.8512 | 277.9211 | 0.0029964 | 0.0030435 | 1.4245e-05 | 1.7906e-05 | 0.068135 | 270.4159 | -0.021765 | -0.025724 | 0.0038509 | 0.005296 | 3.9126e-06 | 1.2763e-06 | 0.00041089 | 0.2461% | 0.1573% | 2.5371 | 109.8961 | 0
280.7859 | 277.2556 | 293.87 | 297.2818 | 277.0389 | 0.013558 | 0.017025 | NoF | 0 | 49.3107 | -201167.6907 | 280.7859 | 277.2556 | 0.0036778 | 0.0041998 | 1.4275e-05 | 1.7888e-05 | 0.078141 | 338.8024 | -0.0010931 | 0.0032426 | -0.0075909 | -0.010919 | 5.4138e-07 | -1.1563e-06 | 0.00058098 | 0.1684% | 0.1585% | 4.0796 | 201.1677 | 0
279.3957 | 277.6217 | 293.9101 | 295.7896 | 277.5944 | 0.013537 | 0.017081 | NoF | 0 | 36.4974 | -100962.6349 | 279.3957 | 277.6217 | 0.004125 | 0.0043694 | 1.424e-05 | 1.794e-05 | 0.05801 | 266.0068 | -0.0036588 | -0.0028651 | -0.023256 | -0.026536 | -1.2835e-06 | 9.3625e-07 | -0.00068323 | 0.2635% | 0.1589% | 2.7663 | 100.9626 | 0
281.4628 | 277.6535 | 291.4612 | 295.0916 | 277.5944 | 0.013564 | 0.016931 | NoF | 0 | 48.3152 | -217081.5734 | 281.4628 | 277.6535 | 0.003127 | 0.00345 | 1.427e-05 | 1.7783e-05 | 0.076244 | 348.7011 | 0.011977 | 0.015733 | -0.0045294 | -0.010016 | 1.0062e-06 | 6.5532e-07 | 0.00019016 | 0.1606% | 0.1578% | 4.493 | 217.0816 | 0
279.6371 | 277.6245 | 291.5059 | 293.5774 | 277.5944 | 0.013555 | 0.016975 | NoF | 0 | 36.2696 | -114683.9759 | 279.6371 | 277.6245 | 0.002923 | 0.0029245 | 1.4265e-05 | 1.7835e-05 | 0.057034 | 271.2941 | -0.003026 | -0.0019748 | -0.00080055 | -0.0011631 | -2.1155e-06 | 1.4523e-06 | -0.00092403 | 0.2366% | 0.1572% | 3.162 | 114.684 | 0
284.6953 | 283.151 | 297.5871 | 299.1621 | 283.15 | 0.013572 | 0.016828 | NoF | 0 | 35.3175 | -87867.6288 | 284.6953 | 283.151 | 0.0030794 | 0.0033672 | 1.4263e-05 | 1.7681e-05 | 0.055818 | 259.8245 | 0.0098959 | 0.01211 | -0.0043738 | -0.010199 | 1.7146e-06 | 4.1779e-07 | -0.00038318 | 0.2957% | 0.158% | 2.4879 | 87.8676 | 0
286.6256 | 283.0832 | 292.2171 | 295.5073 | 283.15 | 0.013598 | 0.016848 | NoF | 0 | 43.9168 | -201837.4757 | 286.6256 | 283.0832 | 0.0029654 | 0.0033459 | 1.4322e-05 | 1.77e-05 | 0.06928 | 338.8019 | 0.003251 | 0.007661 | -0.0017243 | -0.010618 | -3.2597e-06 | -1.0707e-06 | 0.0003182 | 0.1679% | 0.1578% | 4.5959 | 201.8375 | 0
282.4686 | 280.5144 | 302.8174 | 304.8356 | 280.3234 | 0.013565 | 0.016992 | NoF | 0 | 44.989 | -111261.6813 | 282.4686 | 280.5144 | 0.0061578 | 0.0056137 | 1.428e-05 | 1.7845e-05 | 0.075225 | 282.6551 | 0.024223 | 0.022248 | -0.039547 | -0.038558 | 2.7376e-06 | -8.8622e-08 | 0.00073865 | 0.254% | 0.1672% | 2.4731 | 111.2617 | 0
284.7487 | 280.8287 | 297.7124 | 301.4658 | 279.8167 | 0.013586 | 0.016909 | NoF | 0 | 55.5002 | -223371.6162 | 284.7487 | 280.8287 | 0.0029411 | 0.0029788 | 1.4292e-05 | 1.7762e-05 | 0.087281 | 353.0318 | -0.01926 | -0.016018 | -0.00048203 | -0.0029474 | 1.5608e-06 | -1.8828e-06 | -0.00063736 | 0.158% | 0.1573% | 4.0247 | 223.3716 | 0
283.5443 | 279.8208 | 292.2771 | 295.7757 | 279.8167 | 0.013592 | 0.017201 | NoF | 0 | 47.0492 | -212395.5369 | 283.5443 | 279.8208 | 0.003069 | 0.0035592 | 1.4311e-05 | 1.8082e-05 | 0.074292 | 346.387 | 0.0074662 | 0.0096921 | -0.0030525 | -0.0099182 | -2.2451e-06 | 6.8848e-07 | -0.00012613 | 0.1631% | 0.1579% | 4.5143 | 212.3955 | 0
282.3742 | 280.4748 | 292.3634 | 294.2605 | 280.3722 | 0.013574 | 0.016947 | NoF | 0 | 34.6895 | -108218.0277 | 282.3742 | 280.4748 | 0.0036097 | 0.0045909 | 1.4272e-05 | 1.78e-05 | 0.056792 | 281.7857 | 0.012665 | 0.015665 | -0.0052137 | -0.007549 | -3.6956e-07 | -4.2743e-07 | 0.00079121 | 0.2604% | 0.1637% | 3.1196 | 108.218 | 0
281.5702 | 278.2284 | 300.3774 | 303.6549 | 277.5944 | 0.013563 | 0.016973 | NoF | 0 | 56.3491 | -190400.1062 | 281.5702 | 278.2284 | 0.002931 | 0.0029343 | 1.4273e-05 | 1.7832e-05 | 0.088651 | 325.2088 | 0.0034655 | 0.0063639 | -0.00061066 | -0.0012452 | -4.3137e-09 | -1.0134e-06 | -0.00050855 | 0.1708% | 0.1573% | 3.3789 | 190.4001 | 0
279.9294 | 278.002 | 300.1488 | 302.2274 | 277.5944 | 0.013551 | 0.01703 | NoF | 0 | 43.097 | -109778.8685 | 279.9294 | 278.002 | 0.006892 | 0.009437 | 1.424e-05 | 1.7891e-05 | 0.080623 | 305.6336 | 0.026622 | 0.037354 | 0.0029405 | -0.012323 | -1.2431e-06 | -1.6826e-06 | -0.00046632 | 0.2784% | 0.1871% | 2.5472 | 109.7789 | 0
280.867 | 277.3397 | 294.2999 | 297.6792 | 277.0389 | 0.013557 | 0.016985 | NoF | 0 | 49.1535 | -200966.6688 | 280.867 | 277.3397 | 0.0037738 | 0.0043456 | 1.4245e-05 | 1.7848e-05 | 0.078065 | 341.7091 | 0.024273 | 0.029359 | -0.0018538 | -0.0073265 | 2.6587e-07 | 3.9186e-08 | 0.0008753 | 0.17% | 0.1588% | 4.0886 | 200.9667 | 0
281.5033 | 277.8125 | 291.4421 | 294.9814 | 277.5944 | 0.013561 | 0.016902 | NoF | 0 | 46.5063 | -210266.4282 | 281.5033 | 277.8125 | 0.0041833 | 0.0069492 | 1.4269e-05 | 1.775e-05 | 0.076879 | 422.2507 | -0.019298 | -0.0004562 | -0.012952 | -0.028925 | 4.7237e-07 | 5.4675e-06 | -0.0005212 | 0.2008% | 0.1653% | 4.5212 | 210.2664 | 0
279.5734 | 277.6569 | 291.2495 | 293.2273 | 277.5944 | 0.013548 | 0.01696 | NoF | 0 | 34.9742 | -109153.595 | 279.5734 | 277.6569 | 0.0029118 | 0.0029205 | 1.4171e-05 | 1.7715e-05 | 0.054702 | 266.242 | -0.021602 | -0.021518 | -0.0015053 | -0.0026889 | 1.1826e-06 | -3.9136e-06 | 0.00076985 | 0.2439% | 0.1564% | 3.121 | 109.1536 | 0
289.4975 | 283.9184 | 303.1569 | 308.4018 | 282.625 | 0.013616 | 0.016838 | UC | 10 | 83.3485 | -317967.5902 | 289.4975 | 283.9184 | 0.0039671 | 0.0037398 | 1.4322e-05 | 1.7695e-05 | 0.13672 | 445.1566 | -0.0047274 | -0.0063556 | 0.01599 | 0.018799 | -1.2118e-07 | -2.2258e-06 | -0.00040612 | 0.14% | 0.164% | 3.8149 | 317.9676 | -10
285.2089 | 283.3288 | 302.9882 | 304.8701 | 283.15 | 0.013595 | 0.01704 | UC | 10 | 43.1821 | -107136.5349 | 285.2089 | 283.3288 | 0.0031586 | 0.0032765 | 1.4297e-05 | 1.7894e-05 | 0.068641 | 269.5138 | -0.027852 | -0.030164 | -0.0065713 | -0.0046784 | 1.5854e-06 | -1.8472e-06 | 0.0009102 | 0.2516% | 0.159% | 2.481 | 107.1365 | -10
288.9947 | 283.2889 | 297.3038 | 302.665 | 282.5944 | 0.013627 | 0.016787 | UC | 10 | 70.8889 | -325543.3168 | 288.9947 | 283.2889 | 0.0032194 | 0.0033331 | 1.434e-05 | 1.7637e-05 | 0.11166 | 451.5501 | -0.024157 | -0.026683 | -0.011075 | -0.0094415 | 5.972e-08 | 1.6929e-06 | 0.0006926 | 0.1387% | 0.1575% | 4.5923 | 325.5433 | -10
286.8985 | 283.2828 | 297.5716 | 300.9607 | 283.15 | 0.013603 | 0.0169 | UC | 10 | 51.4691 | -206059.9088 | 286.8985 | 283.2828 | 0.002988 | 0.0030083 | 1.4314e-05 | 1.7759e-05 | 0.080946 | 338.7134 | -0.021158 | -0.019527 | -0.00065191 | -0.0016436 | -7.5781e-07 | -1.3426e-06 | 0.00086765 | 0.1644% | 0.1573% | 4.0036 | 206.0599 | -10
284.8264 | 283.2868 | 297.4267 | 298.9828 | 283.15 | 0.013587 | 0.016899 | UC | 10 | 35.3724 | -87691.0759 | 284.8264 | 283.2868 | 0.0035057 | 0.0038687 | 1.4292e-05 | 1.7776e-05 | 0.057261 | 267.207 | 0.026127 | 0.028302 | 0.0050783 | 0.0044859 | -1.6808e-06 | -7.5913e-06 | 0.00025323 | 0.3047% | 0.1619% | 2.4791 | 87.6911 | -10
286.5147 | 283.1143 | 291.783 | 294.9455 | 283.15 | 0.01362 | 0.016956 | UC | 10 | 42.8795 | -194059.4391 | 286.5147 | 283.1143 | 0.0030944 | 0.0032147 | 1.4317e-05 | 1.7808e-05 | 0.067759 | 331.453 | -0.014477 | -0.01847 | -0.0065488 | -0.010947 | -1.899e-06 | -6.5713e-08 | 0.0002322 | 0.1708% | 0.158% | 4.5257 | 194.0594 | -10
285.1974 | 283.1156 | 290.7062 | 292.6385 | 283.15 | 0.013606 | 0.017084 | UC | 10 | 34.0088 | -118729.4647 | 285.1974 | 283.1156 | 0.003342 | 0.0040682 | 1.4305e-05 | 1.7946e-05 | 0.05364 | 280.5376 | 0.0060307 | 0.010062 | -0.0087694 | -0.017064 | -1.717e-06 | -1.8749e-07 | 0.00028189 | 0.2363% | 0.1577% | 3.4911 | 118.7295 | -10
283.9981 | 280.522 | 303.1947 | 306.5783 | 280.3722 | 0.013603 | 0.016995 | UC | 10 | 61.4275 | -198371.3254 | 283.9981 | 280.522 | 0.0029459 | 0.0029508 | 1.4297e-05 | 1.7866e-05 | 0.096627 | 331.3027 | -0.017292 | -0.016975 | -0.0010363 | -0.0021744 | 1.6277e-07 | -1.3504e-06 | -0.00075394 | 0.167% | 0.1573% | 3.2294 | 198.3713 | -10
282.4005 | 280.3766 | 303.0301 | 305.1209 | 280.3722 | 0.013589 | 0.017071 | UC | 10 | 46.2127 | -115438.4903 | 282.4005 | 280.3766 | 0.0039338 | 0.0048828 | 1.4286e-05 | 1.7931e-05 | 0.074707 | 280.3336 | -0.01607 | -0.010394 | 0.0011987 | -0.0043521 | 1.2299e-07 | 5.4439e-07 | 0.0001806 | 0.2428% | 0.1617% | 2.498 | 115.4385 | -10
282.2467 | 280.6029 | 297.3809 | 299.0628 | 280.3539 | 0.013602 | 0.017048 | UC | 10 | 37.0049 | -93852.0524 | 282.2467 | 280.6029 | 0.0030063 | 0.0029568 | 1.4302e-05 | 1.7909e-05 | 0.058394 | 260.2749 | 0.00082603 | 0.00046133 | -0.0064899 | -0.0045464 | 2.0154e-06 | -8.2111e-07 | 0.00058098 | 0.2773% | 0.1578% | 2.5362 | 93.8521 | -10
281.1733 | 277.3523 | 295.0471 | 298.6892 | 277.0389 | 0.013562 | 0.01706 | UC | 10 | 52.791 | -217754.7791 | 281.1733 | 277.3523 | 0.0029377 | 0.0029377 | 1.4262e-05 | 1.7931e-05 | 0.083019 | 347.6568 | -0.00073897 | -0.0011127 | 0.002287 | 0.0025885 | -8.5004e-08 | 1.3468e-06 | -0.00049594 | 0.1597% | 0.1573% | 4.1248 | 217.7548 | -10
279.5859 | 277.5354 | 292.0719 | 294.1836 | 277.5944 | 0.013575 | 0.01704 | UC | 10 | 36.3995 | -117023.5435 | 279.5859 | 277.5354 | 0.0029325 | 0.0029359 | 1.4286e-05 | 1.79e-05 | 0.057242 | 272.6495 | 0.00041886 | 0.00011254 | -0.001074 | -0.002149 | 1.269e-06 | -2.4211e-06 | -0.00097563 | 0.233% | 0.1573% | 3.215 | 117.0235 | -10
289.4874 | 283.792 | 303.3427 | 308.7384 | 282.5944 | 0.013612 | 0.016817 | UC | 20 | 85.1125 | -324502.4336 | 289.4874 | 283.792 | 0.0029202 | 0.0030017 | 1.4324e-05 | 1.7666e-05 | 0.13394 | 448.9747 | -0.0027775 | -0.0033158 | 0.00019961 | 0.0023247 | 1.925e-06 | -1.3384e-07 | 0.00034018 | 0.1384% | 0.1574% | 3.8126 | 324.5024 | -20
285.0077 | 283.1159 | 303.1122 | 305.0083 | 283.15 | 0.013579 | 0.017007 | UC | 20 | 43.2727 | -107681.0161 | 285.0077 | 283.1159 | 0.0029448 | 0.0029518 | 1.4367e-05 | 1.7964e-05 | 0.068426 | 268.5414 | -0.002635 | -0.0021449 | -1.0294e-05 | -0.00098898 | 7.0632e-07 | 9.3217e-08 | -0.00028063 | 0.2494% | 0.1581% | 2.4884 | 107.681 | -20
286.838 | 283.1972 | 297.7759 | 301.2312 | 283.15 | 0.013597 | 0.016827 | UC | 20 | 51.7273 | -207410.8772 | 286.838 | 283.1972 | 0.0029632 | 0.0029555 | 1.4378e-05 | 1.7791e-05 | 0.081797 | 340.823 | -0.00040712 | -0.00024306 | -0.00015811 | 0.0002093 | 1.5172e-06 | -7.3377e-06 | 0.00079125 | 0.1643% | 0.1581% | 4.0097 | 207.4109 | -20
284.3436 | 280.8416 | 303.2966 | 306.6873 | 280.3722 | 0.013578 | 0.016955 | UC | 20 | 61.2355 | -199460.1589 | 284.3436 | 280.8416 | 0.0029732 | 0.0030286 | 1.4294e-05 | 1.7829e-05 | 0.096425 | 332.6248 | -0.029103 | -0.028444 | 0.0019175 | 0.003517 | 1.3528e-06 | -2.1553e-06 | 0.00081414 | 0.1668% | 0.1575% | 3.2573 | 199.4602 | -20
282.2209 | 280.5353 | 297.4835 | 299.1611 | 280.3722 | 0.013574 | 0.017038 | UC | 20 | 37.2756 | -96045.1982 | 282.2209 | 280.5353 | 0.0030596 | 0.0030584 | 1.428e-05 | 1.791e-05 | 0.058617 | 261.4417 | -0.0039014 | -0.0045204 | 0.0056182 | 0.0053087 | -3.9126e-07 | 5.7996e-07 | 0.00069661 | 0.2722% | 0.1573% | 2.5766 | 96.0452 | -20
282.5093 | 280.5132 | 292.3178 | 294.3062 | 280.3722 | 0.01357 | 0.017076 | UC | 20 | 35.6096 | -113690.8423 | 282.5093 | 280.5132 | 0.0031067 | 0.0031998 | 1.4272e-05 | 1.793e-05 | 0.056534 | 280.7794 | -0.031785 | -0.03639 | -0.0062446 | -0.00448 | 3.4002e-07 | -2.5911e-06 | -0.00045772 | 0.247% | 0.1588% | 3.1927 | 113.6908 | -20
281.2636 | 277.8284 | 300.124 | 303.4798 | 277.6555 | 0.013538 | 0.017018 | UC | 20 | 56.0434 | -195400.0188 | 281.2636 | 277.8284 | 0.003099 | 0.0035771 | 1.424e-05 | 1.7879e-05 | 0.088448 | 336.3175 | 0.039469 | 0.049479 | -0.0032192 | -0.012953 | 9.6519e-07 | 4.0995e-08 | 0.00049116 | 0.1721% | 0.1578% | 3.4866 | 195.4 | -20
279.5754 | 277.6342 | 299.9596 | 302.0367 | 277.57 | 0.013547 | 0.017077 | UC | 20 | 43.0141 | -110552.9572 | 279.5754 | 277.6342 | 0.0031684 | 0.0031363 | 1.4245e-05 | 1.7927e-05 | 0.068094 | 269.5956 | 0.013738 | 0.015047 | -0.0058656 | -0.0064596 | 4.2563e-07 | -6.2276e-07 | 0.0009441 | 0.2439% | 0.1583% | 2.5702 | 110.553 | -20
282.9006 | 277.6438 | 291.5501 | 296.4499 | 277.0389 | 0.013574 | 0.016943 | UC | 20 | 59.9766 | -299658.5827 | 282.9006 | 277.6438 | 0.0029435 | 0.0030139 | 1.4268e-05 | 1.7799e-05 | 0.094462 | 423.6553 | 0.0072379 | 0.0079461 | -0.0017965 | -0.0047311 | 1.1732e-06 | 8.8803e-07 | -0.00069565 | 0.1414% | 0.1575% | 4.9963 | 299.6586 | -20
279.8114 | 277.8497 | 291.4498 | 293.4643 | 277.5944 | 0.013531 | 0.017073 | UC | 20 | 35.1645 | -111572.7044 | 279.8114 | 277.8497 | 0.0061149 | 0.0071365 | 1.4229e-05 | 1.794e-05 | 0.061295 | 299.049 | -0.01208 | -0.010128 | -0.031004 | -0.039433 | 2.1788e-06 | 6.3482e-07 | -0.00089823 | 0.268% | 0.1743% | 3.1729 | 111.5727 | -20
289.3771 | 283.552 | 303.3591 | 308.8915 | 282.5944 | 0.01362 | 0.016793 | UC | 30 | 85.5597 | -332135.0311 | 289.3771 | 283.552 | 0.0029264 | 0.002938 | 1.4333e-05 | 1.7634e-05 | 0.13459 | 456.0677 | 0.0017609 | 0.0017508 | 0.00031215 | 0.001703 | -1.3305e-06 | -1.975e-06 | -0.00027234 | 0.1373% | 0.1573% | 3.8819 | 332.135 | -30
284.9557 | 283.3742 | 297.6389 | 299.2231 | 283.15 | 0.013587 | 0.016809 | UC | 30 | 35.5711 | -90067.999 | 284.9557 | 283.3742 | 0.0029499 | 0.0029525 | 1.4284e-05 | 1.7651e-05 | 0.05601 | 258.519 | -0.011306 | -0.010738 | 0.001925 | -8.8821e-05 | -1.0864e-06 | -2.1875e-06 | 0.00085109 | 0.287% | 0.1575% | 2.5321 | 90.068 | -30
282.5399 | 280.5899 | 302.9217 | 304.9293 | 280.3722 | 0.013568 | 0.017006 | UC | 30 | 44.6968 | -111044.4834 | 282.5399 | 280.5899 | 0.002934 | 0.0029285 | 1.4263e-05 | 1.7879e-05 | 0.070287 | 269.2501 | -0.014614 | -0.015231 | -0.0024048 | -0.0019079 | -1.3824e-06 | 1.6639e-07 | 0.00050741 | 0.2425% | 0.1573% | 2.4844 | 111.0445 | -30
281.2294 | 277.7677 | 300.3964 | 303.8275 | 277.5944 | 0.013566 | 0.016982 | UC | 30 | 57.1186 | -197314.282 | 281.2294 | 277.7677 | 0.0030131 | 0.0030475 | 1.4265e-05 | 1.7851e-05 | 0.089879 | 331.0645 | 0.00062483 | -0.00041249 | 0.0044354 | 0.0026443 | -9.9413e-07 | 4.1206e-06 | 0.0009441 | 0.1678% | 0.1574% | 3.4545 | 197.3143 | -30
281.1606 | 277.4255 | 294.981 | 298.5871 | 277.0389 | 0.013574 | 0.016986 | UC | 30 | 51.3509 | -213044.2521 | 281.1606 | 277.4255 | 0.0029555 | 0.0029874 | 1.4274e-05 | 1.7837e-05 | 0.080757 | 343.5984 | -0.0030015 | -0.0026432 | 0.00054096 | -0.0034862 | 4.3768e-07 | 3.6413e-07 | -0.0009957 | 0.1613% | 0.1573% | 4.1488 | 213.0443 | -30
279.7222 | 277.8673 | 295.0071 | 296.939 | 277.5944 | 0.013546 | 0.01704 | UC | 30 | 37.4424 | -105614.1448 | 279.7222 | 277.8673 | 0.0029514 | 0.0029576 | 1.4242e-05 | 1.7899e-05 | 0.058887 | 266.3324 | 0.021956 | 0.019415 | 0.0029877 | 0.00094707 | -8.3377e-07 | 1.1653e-06 | -0.00097754 | 0.2522% | 0.1573% | 2.8207 | 105.6141 | -30
281.5671 | 277.5616 | 292.1773 | 296.0103 | 277.5944 | 0.013574 | 0.016919 | UC | 30 | 49.7695 | -228429.67 | 281.5671 | 277.5616 | 0.0029405 | 0.0029755 | 1.4275e-05 | 1.7756e-05 | 0.078308 | 357.6166 | 0.011067 | 0.011279 | 0.0015735 | -0.001513 | 1.8924e-06 | -6.2216e-07 | -0.00017391 | 0.1566% | 0.1573% | 4.5898 | 228.4297 | -30
279.6179 | 277.6065 | 292.0755 | 294.1519 | 277.5944 | 0.013542 | 0.016966 | UC | 30 | 36.0541 | -114513.3607 | 279.6179 | 277.6065 | 0.0029536 | 0.0029849 | 1.4253e-05 | 1.7827e-05 | 0.056707 | 271.4291 | 0.010701 | 0.011783 | -0.00058873 | -0.0021235 | 1.266e-06 | 8.1206e-07 | 0.00026374 | 0.237% | 0.1573% | 3.1762 | 114.5134 | -30
287.0883 | 283.4784 | 302.8436 | 306.254 | 283.15 | 0.013587 | 0.016931 | UC | 40 | 57.4503 | -205464.7408 | 287.0883 | 283.4784 | 0.0032676 | 0.0036133 | 1.4285e-05 | 1.7782e-05 | 0.098744 | 344.7977 | 0.041556 | 0.028439 | 0.01471 | 0.021876 | -9.5121e-07 | -2.2224e-06 | -6.5637e-05 | 0.1678% | 0.1719% | 3.5764 | 205.4647 | -40
289.4085 | 283.125 | 297.596 | 303.524 | 282.5944 | 0.013588 | 0.016682 | UC | 40 | 75.6907 | -357440.4936 | 289.4085 | 283.125 | 0.0029737 | 0.0029712 | 1.4296e-05 | 1.7552e-05 | 0.1191 | 481.3988 | -0.014014 | -0.014458 | -0.0036545 | -0.0036742 | -9.2842e-07 | -1.3691e-06 | -0.00088772 | 0.1347% | 0.1573% | 4.7224 | 357.4405 | -40
284.8435 | 283.3159 | 297.3253 | 298.8894 | 283.15 | 0.013563 | 0.01682 | UC | 40 | 35.1136 | -86848.7673 | 284.8435 | 283.3159 | 0.0042609 | 0.0046885 | 1.4279e-05 | 1.7676e-05 | 0.055313 | 263.6288 | -0.016939 | -0.021163 | 0.021374 | 0.023327 | 1.6621e-06 | -1.644e-06 | -0.00085905 | 0.3035% | 0.1575% | 2.4734 | 86.8488 | -40
288.0078 | 283.0616 | 294.2924 | 298.8733 | 282.5944 | 0.013584 | 0.016771 | UC | 40 | 56.5103 | -281403.4151 | 288.0078 | 283.0616 | 0.0029691 | 0.0029765 | 1.4286e-05 | 1.7617e-05 | 0.088907 | 405.7547 | -0.0037665 | -0.0051898 | -0.0036832 | -0.0042661 | 1.0219e-06 | -2.0299e-06 | -0.00097946 | 0.1442% | 0.1573% | 4.9797 | 281.4034 | -40
286.4908 | 283.0524 | 291.7523 | 294.9455 | 283.15 | 0.013589 | 0.01688 | UC | 40 | 41.9916 | -195786.3919 | 286.4908 | 283.0524 | 0.0030838 | 0.0033904 | 1.4286e-05 | 1.7726e-05 | 0.066034 | 329.4685 | -0.00099591 | -0.00058077 | -0.0055009 | -0.012651 | -2.11e-06 | 4.9918e-07 | 3.5356e-05 | 0.1683% | 0.1573% | 4.6625 | 195.7864 | -40
285.0855 | 283.0706 | 290.423 | 292.3132 | 283.15 | 0.013566 | 0.017025 | UC | 40 | 33.0531 | -114583.6926 | 285.0855 | 283.0706 | 0.0031855 | 0.0036967 | 1.4271e-05 | 1.7876e-05 | 0.052189 | 275.9481 | -0.005391 | -0.003069 | -0.0073462 | -0.014459 | -2.145e-06 | 5.9081e-08 | 3.7267e-05 | 0.2408% | 0.1579% | 3.4667 | 114.5837 | -40
286.0982 | 280.7049 | 302.9389 | 308.1098 | 279.8167 | 0.013584 | 0.016865 | UC | 40 | 82.2244 | -307144.1862 | 286.0982 | 280.7049 | 0.0029649 | 0.0029309 | 1.4281e-05 | 1.7733e-05 | 0.12933 | 430.7538 | -0.013643 | -0.01209 | -0.0049955 | -0.00067314 | 5.2872e-07 | 1.6862e-06 | 0.00090301 | 0.1402% | 0.1573% | 3.7354 | 307.1442 | -40
282.0287 | 280.4216 | 297.1529 | 298.8325 | 280.3661 | 0.01356 | 0.016975 | UC | 40 | 36.4 | -91484.7828 | 282.0287 | 280.4216 | 0.0029412 | 0.0029274 | 1.4262e-05 | 1.7843e-05 | 0.057238 | 258.4278 | -0.0031067 | -0.0025402 | 0.0026974 | 0.0010978 | -1.0984e-06 | -1.1617e-06 | 0.00095939 | 0.2825% | 0.1572% | 2.5133 | 91.4848 | -40
282.2777 | 280.3715 | 291.6616 | 293.5318 | 280.3722 | 0.013558 | 0.017037 | UC | 40 | 34.0742 | -108485.7629 | 282.2777 | 280.3715 | 0.0030508 | 0.003087 | 1.4256e-05 | 1.7898e-05 | 0.053595 | 267.8507 | -0.019382 | -0.020384 | 0.0012698 | 0.00047778 | 1.2497e-06 | -2.23e-06 | 0.00088581 | 0.2469% | 0.1573% | 3.1838 | 108.4858 | -40
279.862 | 277.9173 | 299.7605 | 301.8288 | 277.5944 | 0.01354 | 0.017054 | UC | 40 | 42.5715 | -110673.6512 | 279.862 | 277.9173 | 0.0029832 | 0.0029843 | 1.4244e-05 | 1.7923e-05 | 0.06695 | 268.4886 | -0.0029453 | -0.0036651 | 0.0033254 | 0.0014854 | -1.2823e-06 | 1.3667e-06 | 0.00048925 | 0.2426% | 0.1573% | 2.5997 | 110.6737 | -40
283.1305 | 278.0023 | 291.4993 | 296.3242 | 277.0389 | 0.013567 | 0.016932 | UC | 40 | 59.5341 | -292130.0771 | 283.1305 | 278.0023 | 0.0029305 | 0.0029345 | 1.4252e-05 | 1.7783e-05 | 0.093659 | 415.8724 | 0.0042101 | 0.0030924 | 0.00050355 | 0.0013375 | -7.061e-07 | -9.0428e-07 | -0.00088883 | 0.1424% | 0.1573% | 4.9069 | 292.1301 | -40
281.6242 | 277.8814 | 291.5716 | 295.1457 | 277.5944 | 0.013546 | 0.016909 | UC | 40 | 46.9936 | -212990.6466 | 281.6242 | 277.8814 | 0.0029176 | 0.0029337 | 1.4172e-05 | 1.7666e-05 | 0.073495 | 341.4087 | 0.0011131 | 0.0003797 | -0.00039944 | -0.0019629 | -1.5247e-06 | -1.1939e-06 | -0.00086317 | 0.1603% | 0.1564% | 4.5323 | 212.9906 | -40
279.687 | 277.7567 | 291.2959 | 293.2949 | 277.5944 | 0.013525 | 0.01693 | UC | 40 | 34.8418 | -109747.6319 | 279.687 | 277.7567 | 0.0029573 | 0.0029532 | 1.414e-05 | 1.7694e-05 | 0.054525 | 266.833 | -0.019614 | -0.018022 | 0.00035859 | -0.0017806 | -3.203e-07 | -1.9218e-06 | -0.00025569 | 0.2431% | 0.1565% | 3.1499 | 109.7476 | -40
286.7684 | 283.2836 | 302.6867 | 306.027 | 283.15 | 0.013584 | 0.016911 | UC | 40 | 56.4979 | -198324.6977 | 286.7684 | 283.2836 | 0.0030884 | 0.0034673 | 1.4291e-05 | 1.7765e-05 | 0.089347 | 332.5462 | 0.01999 | 0.01975 | -0.00075065 | -0.0061719 | -1.9732e-06 | 9.9654e-07 | 0.00026756 | 0.1677% | 0.1581% | 3.5103 | 198.3247 | -40
289.257 | 283.0788 | 297.3394 | 303.1819 | 282.5944 | 0.01361 | 0.016668 | UC | 40 | 73.6295 | -352030.8682 | 289.257 | 283.0788 | 0.0030033 | 0.0030827 | 1.4313e-05 | 1.7522e-05 | 0.11588 | 477.2945 | -0.016168 | -0.019154 | -0.0053581 | -0.0012491 | 1.761e-06 | 2.0069e-06 | 0.00063927 | 0.1356% | 0.1574% | 4.7811 | 352.0309 | -40
284.806 | 283.4539 | 296.579 | 298.062 | 283.15 | 0.013574 | 0.016901 | UC | 40 | 33.2834 | -76933.0569 | 284.806 | 283.4539 | 0.0084512 | 0.010904 | 1.4282e-05 | 1.7777e-05 | 0.14342 | 543.245 | 0.0015326 | 0.0054478 | -0.0062043 | -0.013301 | -1.3474e-06 | 1.6416e-06 | 0.0001376 | 0.7061% | 0.4309% | 2.3115 | 76.9331 | -40
288.0303 | 282.9596 | 294.3938 | 299.1232 | 282.5944 | 0.013599 | 0.016738 | UC | 40 | 57.9058 | -288810.4361 | 288.0303 | 282.9596 | 0.0029647 | 0.0029623 | 1.4299e-05 | 1.7599e-05 | 0.091143 | 414.4741 | -0.012848 | -0.016957 | -0.0049689 | -0.0041089 | 8.2472e-07 | 1.2057e-08 | 0.00013569 | 0.1435% | 0.1574% | 4.9876 | 288.8104 | -40
286.5016 | 283.0361 | 291.7007 | 294.9016 | 283.15 | 0.013584 | 0.016864 | UC | 40 | 42.0475 | -197260.8494 | 286.5016 | 283.0361 | 0.0029507 | 0.0032335 | 1.4289e-05 | 1.7729e-05 | 0.066589 | 334.9751 | -0.0037623 | -0.0043717 | -0.0025482 | -0.0078818 | 1.0785e-06 | -1.4825e-06 | -0.00075776 | 0.1698% | 0.1584% | 4.6914 | 197.2608 | -40
285.0871 | 283.2582 | 290.073 | 291.8291 | 283.15 | 0.013582 | 0.017015 | UC | 40 | 31.8916 | -104124.7492 | 285.0871 | 283.2582 | 0.0035537 | 0.0046587 | 1.4296e-05 | 1.7875e-05 | 0.059229 | 322.7355 | -0.0097027 | -0.012368 | 0.00090301 | -0.00066146 | 2.154e-06 | 1.5554e-07 | 5.3512e-05 | 0.31% | 0.1857% | 3.265 | 104.1247 | -40
283.9963 | 280.6111 | 302.7775 | 306.0954 | 280.3722 | 0.013577 | 0.016929 | UC | 40 | 57.9724 | -192822.8822 | 283.9963 | 280.6111 | 0.0029365 | 0.0029903 | 1.4275e-05 | 1.78e-05 | 0.091186 | 326.8138 | -0.0061682 | -0.0077735 | 0.00059033 | -3.5568e-05 | 1.5554e-06 | 1.7978e-06 | 0.00019111 | 0.1695% | 0.1573% | 3.3261 | 192.8229 | -40
286.493 | 280.4507 | 297.1641 | 302.8997 | 279.8167 | 0.013603 | 0.016829 | UC | 40 | 75.8831 | -344570.059 | 286.493 | 280.4507 | 0.002968 | 0.0030058 | 1.4297e-05 | 1.77e-05 | 0.12213 | 468.5656 | -0.00026544 | -0.0038053 | 0.0027462 | 0.0070165 | -7.4635e-07 | -1.2618e-06 | -0.00058672 | 0.136% | 0.161% | 4.5408 | 344.5701 | -40
283.2962 | 279.9882 | 297.0792 | 300.3437 | 279.8533 | 0.013574 | 0.016932 | UC | 40 | 49.0105 | -188443.9568 | 283.2962 | 279.9882 | 0.0045797 | 0.0063652 | 1.4273e-05 | 1.7794e-05 | 0.081773 | 353.9356 | -0.014234 | -0.00084992 | -0.013256 | -0.029527 | 5.0762e-07 | -1.0671e-07 | -0.00070712 | 0.1878% | 0.1668% | 3.845 | 188.444 | -40
282.0087 | 280.3651 | 297.0781 | 298.8205 | 280.3722 | 0.013558 | 0.016962 | UC | 40 | 36.6484 | -93549.1739 | 282.0087 | 280.3651 | 0.0034181 | 0.0038541 | 1.425e-05 | 1.783e-05 | 0.058585 | 263.2592 | -0.0097696 | -0.0065228 | -0.0062202 | -0.010205 | 2.7491e-07 | -2.6189e-06 | 8.5045e-05 | 0.2814% | 0.1599% | 2.5526 | 93.5492 | -40
286.1744 | 280.2874 | 294.3926 | 299.9419 | 279.8167 | 0.013587 | 0.016822 | UC | 40 | 68.7009 | -335375.9096 | 286.1744 | 280.2874 | 0.0030247 | 0.0031463 | 1.4282e-05 | 1.7679e-05 | 0.10821 | 459.5377 | -0.0078818 | -0.0086691 | -0.0048798 | -0.0061491 | -7.4876e-07 | 2.0763e-06 | 0.00087721 | 0.137% | 0.1575% | 4.8817 | 335.3759 | -40
281.3151 | 277.9432 | 299.7866 | 303.1328 | 277.5944 | 0.013569 | 0.016999 | UC | 40 | 56.3311 | -192229.7127 | 281.3151 | 277.9432 | 0.0029221 | 0.0029325 | 1.4269e-05 | 1.7864e-05 | 0.088882 | 326.0589 | 0.0036651 | 0.0034676 | 0.0015926 | 0.002253 | -3.6896e-07 | 1.6561e-06 | 0.00011467 | 0.1696% | 0.1578% | 3.4125 | 192.2297 | -40
279.5245 | 277.5505 | 299.7649 | 301.8674 | 277.6555 | 0.013534 | 0.017052 | UC | 40 | 43.2324 | -112313.672 | 279.5245 | 277.5505 | 0.0029308 | 0.0029311 | 1.4224e-05 | 1.7921e-05 | 0.067982 | 269.3199 | -0.001969 | -0.0015523 | 0.0020343 | 0.0012762 | -1.2226e-06 | -2.5501e-07 | -0.00082465 | 0.2398% | 0.1572% | 2.5979 | 112.3137 | -40
280.8937 | 277.3933 | 293.8264 | 297.2435 | 277.0389 | 0.013556 | 0.017027 | UC | 40 | 49.4981 | -199407.2776 | 280.8937 | 277.3933 | 0.0030032 | 0.0031587 | 1.425e-05 | 1.7876e-05 | 0.077839 | 332.0327 | -0.0016712 | -0.00069863 | -0.002442 | -0.0084716 | 1.5669e-06 | -6.9089e-07 | -0.00086765 | 0.1665% | 0.1573% | 4.0286 | 199.4073 | -40
279.6319 | 278.0214 | 293.0977 | 294.8396 | 277.5944 | 0.013554 | 0.017079 | UC | 40 | 34.747 | -91770.0216 | 279.6319 | 278.0214 | 0.0081943 | 0.010572 | 1.4247e-05 | 1.794e-05 | 0.15183 | 539.7179 | -0.0015746 | 0.0056734 | -0.019141 | -0.027105 | -1.7718e-06 | -1.6157e-07 | -0.00094028 | 0.5881% | 0.4369% | 2.6411 | 91.77 | -40
282.7151 | 277.7847 | 290.7239 | 295.3523 | 277.0389 | 0.013575 | 0.016943 | UC | 40 | 57.2205 | -281075.4835 | 282.7151 | 277.7847 | 0.0029848 | 0.002988 | 1.4287e-05 | 1.7802e-05 | 0.090021 | 405.6507 | 0.0086808 | 0.0090195 | -0.0041429 | -0.0033593 | 1.6591e-06 | 2.2909e-06 | 0.00057716 | 0.1443% | 0.1573% | 4.9121 | 281.0755 | -40
280.9172 | 277.5601 | 289.7252 | 292.9335 | 277.5944 | 0.013562 | 0.016954 | UC | 40 | 42.44 | -191331.4235 | 280.9172 | 277.5601 | 0.0030458 | 0.0031297 | 1.4257e-05 | 1.7808e-05 | 0.066773 | 325.833 | 0.015484 | 0.013411 | -0.00092424 | -0.0024877 | -1.1762e-06 | -1.4975e-06 | -0.00099188 | 0.1703% | 0.1573% | 4.5083 | 191.3314 | -40
279.4461 | 277.8225 | 289.2549 | 290.9529 | 277.5944 | 0.01355 | 0.016975 | UC | 40 | 31.4876 | -92482.9389 | 279.4461 | 277.8225 | 0.0037899 | 0.0034074 | 1.4242e-05 | 1.7831e-05 | 0.049561 | 261.294 | -0.0079986 | -0.0073281 | -0.011129 | -0.0079657 | -9.037e-07 | -9.6881e-07 | -0.00037649 | 0.2825% | 0.1574% | 2.9371 | 92.4829 | -40
286.8916 | 283.4214 | 297.6888 | 301.0009 | 283.15 | 0.013596 | 0.016886 | OC | 10 | 50.8607 | -197667.2088 | 286.8916 | 283.4214 | 0.0034499 | 0.0049931 | 1.4304e-05 | 1.7743e-05 | 0.084335 | 354.5762 | 0.0079116 | 0.012575 | 0.0040983 | -0.0043972 | 2.3259e-06 | 6.2578e-07 | -0.00091161 | 0.1794% | 0.1658% | 3.8864 | 197.6672 | 10
284.6546 | 283.0837 | 297.6448 | 299.2488 | 283.15 | 0.013599 | 0.016866 | OC | 10 | 36.1904 | -89564.3403 | 284.6546 | 283.0837 | 0.0029582 | 0.0029453 | 1.4307e-05 | 1.7721e-05 | 0.05691 | 257.6423 | -0.001805 | -0.0028455 | 0.0039199 | 0.0025312 | -3.622e-06 | -3.1952e-07 | -0.00078165 | 0.2877% | 0.1573% | 2.4748 | 89.5643 | 10
287.9697 | 282.7974 | 294.8574 | 299.7073 | 282.5944 | 0.013618 | 0.016795 | OC | 10 | 62.3167 | -295030.5551 | 287.9697 | 282.7974 | 0.0030223 | 0.0030941 | 1.4316e-05 | 1.765e-05 | 0.098033 | 419.247 | 0.0096656 | 0.0087694 | 0.00044805 | -0.002391 | -2.7672e-07 | -6.6135e-07 | -0.00066316 | 0.1421% | 0.1573% | 4.7344 | 295.0306 | 10
286.6266 | 283.0395 | 292.2103 | 295.5561 | 283.15 | 0.013619 | 0.016923 | OC | 10 | 45.139 | -204687.7739 | 286.6266 | 283.0395 | 0.0029479 | 0.0031119 | 1.4325e-05 | 1.7776e-05 | 0.070995 | 338.0078 | 0.0011573 | 0.0053294 | -0.0006604 | -0.0068461 | -9.887e-08 | 1.1177e-06 | 0.00043574 | 0.1651% | 0.1573% | 4.5346 | 204.6878 | 10
283.8472 | 280.4259 | 303.1304 | 306.4787 | 279.8167 | 0.01359 | 0.016975 | OC | 10 | 61.6515 | -195078.2154 | 283.8472 | 280.4259 | 0.0029861 | 0.0030052 | 1.4289e-05 | 1.7831e-05 | 0.097124 | 329.0349 | -0.029197 | -0.030353 | -0.0035563 | -0.0013739 | -1.5807e-06 | 3.059e-06 | -0.00029336 | 0.1687% | 0.1575% | 3.1642 | 195.0782 | 10
282.2661 | 280.6237 | 297.4568 | 299.131 | 280.3722 | 0.01358 | 0.017012 | OC | 10 | 37.2785 | -93623.7558 | 282.2661 | 280.6237 | 0.0031292 | 0.0030743 | 1.4286e-05 | 1.787e-05 | 0.058647 | 261.4165 | -0.00019483 | -0.0025604 | 0.0072188 | 0.004446 | 1.31e-06 | -1.7935e-06 | -5.0645e-05 | 0.2792% | 0.1573% | 2.5115 | 93.6238 | 10
279.5814 | 277.7703 | 294.915 | 296.8045 | 277.5944 | 0.013561 | 0.017045 | OC | 10 | 37.739 | -103243.6493 | 279.5814 | 277.7703 | 0.0030634 | 0.0031173 | 1.426e-05 | 1.7909e-05 | 0.059358 | 264.9237 | -0.0083941 | -0.0094389 | 0.0057552 | 0.0066847 | -7.0536e-07 | 2.0287e-06 | -0.00020258 | 0.2566% | 0.1573% | 2.7357 | 103.2436 | 10
279.5077 | 277.5353 | 291.4566 | 293.4967 | 277.5944 | 0.01357 | 0.016988 | OC | 10 | 36.0199 | -112517.272 | 279.5077 | 277.5353 | 0.0069757 | 0.0057502 | 1.4269e-05 | 1.7842e-05 | 0.056963 | 280.0333 | 0.010205 | 0.0059542 | -0.032011 | -0.024954 | -1.2636e-06 | -9.9534e-07 | 0.00075012 | 0.2489% | 0.1581% | 3.1238 | 112.5173 | 10
285.2272 | 283.3627 | 302.8593 | 304.7632 | 283.15 | 0.013576 | 0.016973 | OC | 20 | 43.0881 | -106093.6893 | 285.2272 | 283.3627 | 0.0029748 | 0.0029867 | 1.4362e-05 | 1.793e-05 | 0.068417 | 269.4304 | -0.022218 | -0.026069 | -0.00062674 | -0.00014784 | -1.4691e-07 | 1.1835e-06 | 0.00027271 | 0.254% | 0.1588% | 2.4622 | 106.0937 | 20
286.9051 | 283.3443 | 297.5481 | 300.9521 | 283.15 | 0.013591 | 0.016753 | OC | 20 | 51.4985 | -202746.5487 | 286.9051 | 283.3443 | 0.0029699 | 0.0029732 | 1.4298e-05 | 1.7596e-05 | 0.080996 | 335.0016 | -0.0085237 | -0.0084833 | 0.0011 | -0.00023995 | -7.6625e-07 | 1.5705e-06 | 0.00053416 | 0.1652% | 0.1573% | 3.9369 | 202.7465 | 20
286.6576 | 283.0949 | 292.1981 | 295.5438 | 283.15 | 0.013593 | 0.016858 | OC | 20 | 44.9203 | -202917.9708 | 286.6576 | 283.0949 | 0.003154 | 0.0040342 | 1.4302e-05 | 1.7707e-05 | 0.07111 | 342.7452 | -0.002073 | 0.0017391 | -0.0061512 | -0.016621 | -2.0877e-06 | 2.8305e-06 | 0.00098041 | 0.1689% | 0.1583% | 4.5173 | 202.918 | 20
285.1634 | 282.9825 | 291.0973 | 293.1554 | 283.0401 | 0.013597 | 0.017028 | OC | 20 | 35.2411 | -124305.7378 | 285.1634 | 282.9825 | 0.0032478 | 0.0035428 | 1.4297e-05 | 1.7944e-05 | 0.05618 | 279.6703 | -0.0033381 | 0.0019233 | -0.012789 | -0.017274 | 2.0606e-06 | 4.8899e-06 | -0.00060774 | 0.225% | 0.1594% | 3.5273 | 124.3057 | 20
282.6134 | 280.691 | 302.8193 | 304.8194 | 280.3722 | 0.013577 | 0.017 | OC | 20 | 45.0149 | -109535.7623 | 282.6134 | 280.691 | 0.0046421 | 0.0061542 | 1.4285e-05 | 1.7862e-05 | 0.07747 | 290.2711 | 0.01226 | 0.015965 | -0.010587 | -0.014173 | 2.1625e-06 | 2.2125e-07 | -4.0134e-05 | 0.265% | 0.1721% | 2.4333 | 109.5358 | 20
283.4671 | 279.7971 | 291.912 | 295.3345 | 279.8167 | 0.013587 | 0.017226 | OC | 20 | 46.7643 | -209267.2428 | 283.4671 | 279.7971 | 0.004085 | 0.0059488 | 1.4282e-05 | 1.8094e-05 | 0.07365 | 351.8269 | -0.0016064 | 0.0045814 | -0.015218 | -0.031801 | -9.3143e-07 | -9.9172e-07 | 0.00051027 | 0.1681% | 0.1575% | 4.4749 | 209.2672 | 20
282.2289 | 280.3655 | 291.8173 | 293.6766 | 280.3722 | 0.013569 | 0.016977 | OC | 20 | 34.5686 | -106136.1342 | 282.2289 | 280.3655 | 0.0030529 | 0.0031761 | 1.4265e-05 | 1.7832e-05 | 0.054832 | 268.8015 | 0.0018681 | 0.0036641 | -0.00032595 | -0.0003026 | 1.2021e-06 | 9.3987e-07 | 0.00023794 | 0.2533% | 0.1586% | 3.0703 | 106.1361 | 20
281.524 | 278.1705 | 300.1274 | 303.4502 | 277.6555 | 0.013559 | 0.016983 | OC | 20 | 57.4398 | -191010.0537 | 281.524 | 278.1705 | 0.002931 | 0.0029404 | 1.4271e-05 | 1.7841e-05 | 0.090375 | 325.182 | -0.012466 | -0.012747 | -3.3976e-05 | 0.00072411 | -4.4353e-06 | -3.3158e-08 | -0.00050741 | 0.1702% | 0.1573% | 3.3254 | 191.0101 | 20
280.7051 | 277.1949 | 294.0845 | 297.5159 | 277.0389 | 0.013547 | 0.016996 | OC | 20 | 50.4241 | -199859.2206 | 280.7051 | 277.1949 | 0.0029628 | 0.0029849 | 1.4238e-05 | 1.785e-05 | 0.079321 | 332.5297 | 0.0081558 | 0.0099379 | -0.00047354 | -0.0034337 | -7.8674e-07 | 1.7061e-06 | -0.00063258 | 0.1664% | 0.1573% | 3.9636 | 199.8592 | 20
279.4198 | 277.6593 | 294.0994 | 295.9679 | 277.5944 | 0.013543 | 0.017047 | OC | 20 | 36.6698 | -100235.1316 | 279.4198 | 277.6593 | 0.0030258 | 0.0030399 | 1.4243e-05 | 1.7916e-05 | 0.057736 | 262.9852 | 0.0058141 | 0.0057069 | 8.9186e-05 | -0.0029458 | 1.2311e-06 | 1.6428e-06 | 0.00096894 | 0.2624% | 0.1574% | 2.7335 | 100.2351 | 20
281.56 | 277.9241 | 291.3726 | 294.8777 | 277.5944 | 0.01357 | 0.01691 | OC | 20 | 47.4501 | -207277.7753 | 281.56 | 277.9241 | 0.00308 | 0.0031615 | 1.4262e-05 | 1.7785e-05 | 0.074729 | 339.9183 | -0.0069204 | -0.0097797 | -0.0010171 | -0.00031162 | 1.3577e-06 | 1.0014e-06 | -0.00055327 | 0.164% | 0.1575% | 4.3683 | 207.2778 | 20
279.7784 | 277.8261 | 291.7462 | 293.7739 | 277.5944 | 0.013537 | 0.016943 | OC | 20 | 36.2916 | -111088.3421 | 279.7784 | 277.8261 | 0.0030525 | 0.0030947 | 1.4236e-05 | 1.7792e-05 | 0.057117 | 270.3166 | -0.026472 | -0.02737 | 0.0039996 | 0.0022297 | -1.6886e-06 | -1.7302e-07 | -0.00058194 | 0.2433% | 0.1574% | 3.061 | 111.0883 | 20
287.0063 | 283.5676 | 302.7763 | 306.3588 | 282.5944 | 0.013594 | 0.016993 | OC | 30 | 61.9598 | -195822.6862 | 287.0063 | 283.5676 | 0.0029377 | 0.0030431 | 1.4305e-05 | 1.7853e-05 | 0.097481 | 329.3083 | 0.0046067 | 0.0044801 | 0.0024163 | 0.0021858 | -4.1547e-07 | -1.2552e-06 | -0.00044083 | 0.1682% | 0.1573% | 3.1605 | 195.8227 | 30
286.8141 | 283.4049 | 297.3981 | 300.8627 | 283.15 | 0.013592 | 0.016821 | OC | 30 | 52.0383 | -194122.6591 | 286.8141 | 283.4049 | 0.0029815 | 0.0030347 | 1.439e-05 | 1.7782e-05 | 0.082286 | 329.7383 | -0.011536 | -0.010582 | -7.6508e-05 | 0.0017278 | -3.2855e-07 | -8.0064e-06 | 0.00070824 | 0.1699% | 0.1581% | 3.7304 | 194.1227 | 30
284.654 | 283.106 | 297.3562 | 299.0484 | 283.15 | 0.013585 | 0.016846 | OC | 30 | 36.3382 | -88157.3459 | 284.654 | 283.106 | 0.0032701 | 0.0031329 | 1.4293e-05 | 1.769e-05 | 0.057156 | 258.6258 | -0.017804 | -0.020605 | 0.012463 | 0.0085125 | -2.8648e-06 | 1.4776e-06 | -0.00032776 | 0.2934% | 0.1573% | 2.426 | 88.1573 | 30
286.5993 | 283.1772 | 291.8946 | 295.2602 | 283.15 | 0.013587 | 0.016904 | OC | 30 | 44.6202 | -194822.5313 | 286.5993 | 283.1772 | 0.0033668 | 0.0045046 | 1.4293e-05 | 1.7767e-05 | 0.070895 | 340.6042 | 0.0056968 | 0.012091 | -0.0038483 | -0.017778 | -1.5234e-06 | 3.1319e-06 | -3.9178e-05 | 0.1748% | 0.1589% | 4.3662 | 194.8225 | 30
285.1114 | 280.5672 | 300.5208 | 305.04 | 279.8167 | 0.013582 | 0.016984 | OC | 30 | 70.3644 | -258854.2682 | 285.1114 | 280.5672 | 0.0029645 | 0.0031871 | 1.4286e-05 | 1.7846e-05 | 0.1107 | 384.8749 | -0.024183 | -0.026262 | -0.0024139 | 0.0070935 | 8.5065e-07 | -1.3082e-06 | -0.0008151 | 0.1487% | 0.1573% | 3.6788 | 258.8543 | 30
282.2974 | 280.3546 | 292.4126 | 294.4348 | 280.3722 | 0.013562 | 0.016956 | OC | 30 | 35.7657 | -110593.6115 | 282.2974 | 280.3546 | 0.0034132 | 0.0038314 | 1.4264e-05 | 1.7826e-05 | 0.058409 | 278.1971 | -0.011515 | -0.013454 | 0.0013022 | 0.00026862 | -3.1325e-06 | 1.1039e-06 | -0.00014238 | 0.2515% | 0.1633% | 3.0922 | 110.5936 | 30
279.6389 | 277.6612 | 300.3284 | 302.4505 | 277.5944 | 0.013542 | 0.017007 | OC | 30 | 44.8725 | -112582.739 | 279.6389 | 277.6612 | 0.0032208 | 0.0032088 | 1.4244e-05 | 1.7855e-05 | 0.070611 | 270.6654 | -0.014306 | -0.018456 | 0.0058725 | 0.0049928 | -3.9343e-06 | 2.1034e-06 | -0.0001634 | 0.2404% | 0.1574% | 2.5089 | 112.5827 | 30
279.3856 | 277.6435 | 294.2396 | 296.1137 | 277.5944 | 0.013545 | 0.017046 | OC | 30 | 36.7807 | -99206.7712 | 279.3856 | 277.6435 | 0.0035932 | 0.0038077 | 1.424e-05 | 1.7908e-05 | 0.057906 | 263.1722 | -0.015682 | -0.016799 | -0.01677 | -0.02073 | -1.3167e-06 | 2.8058e-06 | -0.00057334 | 0.2653% | 0.1574% | 2.6973 | 99.2068 | 30
282.8115 | 277.9302 | 291.0756 | 295.802 | 277.0389 | 0.013568 | 0.016901 | OC | 30 | 58.7824 | -278127.1992 | 282.8115 | 277.9302 | 0.0032062 | 0.0031153 | 1.4265e-05 | 1.7767e-05 | 0.092635 | 412.4662 | 0.018821 | 0.016783 | -0.012612 | -0.0053719 | 2.2493e-06 | 1.5572e-06 | -0.00043287 | 0.1483% | 0.1576% | 4.7315 | 278.1272 | 30
279.5343 | 277.611 | 291.2667 | 293.28 | 277.5944 | 0.013551 | 0.016951 | OC | 30 | 35.5443 | -109568.755 | 279.5343 | 277.611 | 0.0031724 | 0.0034694 | 1.4255e-05 | 1.7806e-05 | 0.05643 | 271.1525 | -0.0079418 | -0.0083474 | 0.0060392 | 0.0060312 | -1.9967e-06 | 1.3366e-06 | -0.00062781 | 0.2475% | 0.1588% | 3.0826 | 109.5688 | 30
289.5277 | 284.8142 | 302.7595 | 307.6043 | 282.6005 | 0.013598 | 0.016853 | OC | 40 | 78.0202 | -268251.2897 | 289.5277 | 284.8142 | 0.0029348 | 0.0029898 | 1.4301e-05 | 1.7728e-05 | 0.12277 | 393.3409 | -0.0058587 | -0.004833 | -0.0019281 | -0.00031905 | -1.943e-06 | -2.9281e-06 | -0.00065074 | 0.1466% | 0.1574% | 3.4382 | 268.2513 | 40
286.2709 | 282.6626 | 303.1264 | 306.9824 | 282.5944 | 0.013569 | 0.016923 | OC | 40 | 66.2487 | -205180.5265 | 286.2709 | 282.6626 | 0.0029291 | 0.0030159 | 1.4276e-05 | 1.779e-05 | 0.10424 | 336.656 | 0.011004 | 0.0092159 | -0.00047354 | 0.0021235 | -2.1058e-06 | 9.242e-07 | 0.00082083 | 0.1641% | 0.1573% | 3.0971 | 205.1805 | 40
285.4006 | 283.5238 | 303.1318 | 305.2244 | 283.15 | 0.013574 | 0.016975 | OC | 40 | 45.088 | -106773.5475 | 285.4006 | 283.5238 | 0.003368 | 0.0036187 | 1.4353e-05 | 1.7939e-05 | 0.072948 | 272.1195 | -0.023207 | -0.024732 | 0.0045252 | 0.0058863 | -2.1951e-06 | 1.9207e-06 | -0.00088374 | 0.2549% | 0.1618% | 2.3681 | 106.7735 | 40
286.9814 | 283.458 | 297.6877 | 301.4047 | 283.15 | 0.013586 | 0.016832 | OC | 40 | 54.6137 | -200538.2471 | 286.9814 | 283.458 | 0.0029655 | 0.003193 | 1.4298e-05 | 1.7678e-05 | 0.085884 | 333.415 | -0.034163 | -0.032516 | -0.0030111 | -0.0095429 | 3.4364e-07 | -9.3384e-07 | 0.00045772 | 0.1663% | 0.1573% | 3.6719 | 200.5382 | 40
284.691 | 283.1457 | 297.4741 | 299.2214 | 283.15 | 0.013555 | 0.016877 | OC | 40 | 36.5395 | -87817.2559 | 284.691 | 283.1457 | 0.0034953 | 0.0040556 | 1.4268e-05 | 1.7729e-05 | 0.060164 | 270.028 | -0.0057716 | -0.0066773 | 0.0077199 | 0.0076934 | -1.0876e-06 | -2.5574e-06 | -0.00054372 | 0.3075% | 0.1647% | 2.4034 | 87.8173 | 40
286.6121 | 283.1362 | 291.9849 | 295.5484 | 283.15 | 0.013581 | 0.016876 | OC | 40 | 46.7515 | -197800.5322 | 286.6121 | 283.1362 | 0.0029442 | 0.003034 | 1.4271e-05 | 1.7731e-05 | 0.073519 | 330.455 | -0.0026947 | -0.0037755 | -0.0029856 | -0.0065589 | 7.6263e-07 | 1.506e-06 | -0.00096703 | 0.1671% | 0.1573% | 4.2309 | 197.8005 | 40
284.0932 | 280.7379 | 302.8783 | 306.5288 | 279.8167 | 0.013563 | 0.016974 | OC | 40 | 65.6464 | -190914.0394 | 284.0932 | 280.7379 | 0.0029823 | 0.0030648 | 1.4254e-05 | 1.7832e-05 | 0.10325 | 325.4226 | -0.024175 | -0.023221 | 0.00068429 | 0.0024457 | -1.9183e-06 | -1.6452e-06 | 0.00052843 | 0.1705% | 0.1573% | 2.9082 | 190.914 | 40
284.4914 | 280.7979 | 297.5115 | 301.4411 | 279.8167 | 0.013587 | 0.016943 | OC | 40 | 58.1627 | -210487.6718 | 284.4914 | 280.7979 | 0.0031364 | 0.0038696 | 1.4276e-05 | 1.7808e-05 | 0.091509 | 342.9693 | -0.041172 | -0.036511 | -0.0064166 | -0.016688 | -5.0641e-08 | -2.6448e-06 | 0.00092785 | 0.1629% | 0.1573% | 3.6189 | 210.4877 | 40
282.0807 | 280.4472 | 297.4814 | 299.3455 | 280.3722 | 0.013562 | 0.016971 | OC | 40 | 38.4913 | -92996.5628 | 282.0807 | 280.4472 | 0.0029854 | 0.0031358 | 1.4192e-05 | 1.7741e-05 | 0.060472 | 258.0569 | -0.0010028 | -0.0013455 | 0.0037709 | 0.0038253 | -4.5915e-06 | 4.4778e-07 | -1.2022e-05 | 0.2775% | 0.1571% | 2.416 | 92.9966 | 40
279.5588 | 277.5836 | 300.3383 | 302.4651 | 277.5944 | 0.013537 | 0.017018 | OC | 40 | 44.7598 | -112408.473 | 279.5588 | 277.5836 | 0.0029836 | 0.0030669 | 1.4157e-05 | 1.7779e-05 | 0.070177 | 268.405 | 0.0063339 | 0.0067296 | 0.0019141 | -0.00169 | 2.9536e-07 | -1.1499e-06 | 0.00068557 | 0.2388% | 0.1568% | 2.5114 | 112.4085 | 40
281.3109 | 277.7153 | 294.9295 | 298.6486 | 277.0389 | 0.013563 | 0.016995 | OC | 40 | 53.577 | -204896.5795 | 281.3109 | 277.7153 | 0.0029353 | 0.0031045 | 1.4189e-05 | 1.776e-05 | 0.083815 | 334.8614 | -0.00956 | -0.011038 | 0.0015114 | -0.0025104 | -2.371e-06 | -1.4591e-06 | -0.00014703 | 0.1634% | 0.1564% | 3.8243 | 204.8966 | 40
10.1421 |  | 14.1042 |  |  | 0.0075118 | 0.032885 | [22 empty] | 280.5074
Must be accounted for |  | Must be accounted for |  |  | Can be omitted | Can be omitted | [22 empty] | Must be accounted for
279.3856 |  | 289.2549 | [26 empty] | 76.9331
289.5277 |  | 303.3591 | [26 empty] | 357.4405

## test_file_00
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level | TEI_K_mean | TCI_K_mean | Cooling capacity [kW] | kW_mean | SUMMARY OUTPUT | [9 empty] | Test case | TEI_K_mean | TCI_K_mean | Cooling capacity [kW] | Est kW
287.0211 | 283.5728 | 302.7232 | 305.9926 | 283.15 | 0.013574 | 0.01687 | NoF | 0 | 57.5337 | -196083.8885 | 287.0211 | 283.5728 | 0.0035352 | 0.0032638 | 1.4289e-05 | 1.7738e-05 | 0.090939 | 331.1712 | 0.0081956 | 0.0070162 | 0.012345 | 0.012525 | 6.9955e-07 | -2.4459e-06 | 0.00080527 | 0.1689% | 0.1581% | 3.4082 | 196.0839 | 0 | 287.0211 | 302.7232 | 196.0839 | 57.5337 | [11 empty] | 280 | 292 | 77 | 29.7066
285.1628 | 283.2962 | 302.6607 | 304.5239 | 283.15 | 0.013574 | 0.016943 | NoF | 0 | 42.4033 | -106201.144 | 285.1628 | 283.2962 | 0.0034386 | 0.0042815 | 1.4276e-05 | 1.7799e-05 | 0.068925 | 280.7022 | 0.013549 | 0.019668 | -0.0016335 | -0.01023 | 1.205e-07 | -5.9568e-07 | 0.00085124 | 0.2643% | 0.1625% | 2.5045 | 106.2011 | 0 | 285.1628 | 302.6607 | 106.2011 | 42.4033 | Regression Statistics | [10 empty] | 290 | 303 | 358 | 79.5444
289.3396 | 283.2563 | 297.3904 | 303.1459 | 282.5944 | 0.013614 | 0.016704 | NoF | 0 | 75.9413 | -346708.8515 | 289.3396 | 283.2563 | 0.0031795 | 0.0034681 | 1.4313e-05 | 1.7548e-05 | 0.11968 | 475.8415 | -0.025143 | -0.031243 | -0.0098445 | -0.005959 | 7.6866e-07 | 1.0574e-06 | 0.00058385 | 0.1372% | 0.1576% | 4.5655 | 346.7089 | 0 | 289.3396 | 297.3904 | 346.7089 | 75.9413 | Multiple R | 0.99011
284.9085 | 283.3896 | 297.1093 | 298.6959 | 283.15 | 0.013572 | 0.01683 | NoF | 0 | 35.0978 | -86416.0624 | 284.9085 | 283.3896 | 0.004789 | 0.0056103 | 1.4275e-05 | 1.7684e-05 | 0.060402 | 273.6682 | 0.0016149 | 0.00010352 | -0.010847 | -0.01864 | 1.3926e-06 | 1.1925e-06 | -7.1667e-05 | 0.3167% | 0.1721% | 2.4622 | 86.4161 | 0 | 284.9085 | 297.1093 | 86.4161 | 35.0978 | R Square | 0.98032
288.2445 | 283.1384 | 294.5706 | 299.32 | 282.5944 | 0.013593 | 0.016774 | NoF | 0 | 60.5082 | -290664.1768 | 288.2445 | 283.1384 | 0.00301 | 0.0030414 | 1.43e-05 | 1.7618e-05 | 0.095309 | 415.0542 | -0.015969 | -0.015078 | -0.0053639 | -0.0040643 | 3.1229e-07 | 1.6398e-06 | -0.00075872 | 0.1428% | 0.1575% | 4.8037 | 290.6642 | 0 | 288.2445 | 294.5706 | 290.6642 | 60.5082 | Adjusted R Square | 0.97786
286.4847 | 283.1062 | 291.6634 | 294.7821 | 283.15 | 0.013593 | 0.016907 | NoF | 0 | 42.4875 | -192431.2297 | 286.4847 | 283.1062 | 0.0029399 | 0.0030077 | 1.4289e-05 | 1.7756e-05 | 0.066811 | 326.2953 | -0.00059457 | -0.00031003 | -0.00044381 | -0.0050624 | -2.8793e-06 | 1.6091e-06 | -0.00085332 | 0.1696% | 0.1572% | 4.5291 | 192.4312 | 0 | 286.4847 | 291.6634 | 192.4312 | 42.4875 | Standard Error | 1.4607
285.116 | 283.2578 | 290.0515 | 291.8041 | 283.15 | 0.013583 | 0.017029 | NoF | 0 | 32.2977 | -105801.7462 | 285.116 | 283.2578 | 0.0030693 | 0.0034222 | 1.428e-05 | 1.7882e-05 | 0.052047 | 275.889 | 0.015505 | 0.018688 | 0.0019594 | -0.0016754 | 2.1981e-06 | 2.1522e-07 | -0.0007377 | 0.2608% | 0.1611% | 3.2758 | 105.8017 | 0 | 285.116 | 290.0515 | 105.8017 | 32.2977 | Observations | 28
282.5718 | 280.5848 | 302.7032 | 304.748 | 280.3722 | 0.01356 | 0.01697 | NoF | 0 | 45.3258 | -113082.5014 | 282.5718 | 280.5848 | 0.0030708 | 0.0030267 | 1.4278e-05 | 1.7837e-05 | 0.071285 | 270.0064 | -0.011196 | -0.011273 | 0.0055513 | 0.0027987 | 8.3799e-07 | 3.5991e-07 | -0.00054181 | 0.2388% | 0.1573% | 2.4949 | 113.0825 | 0 | 282.5718 | 302.7032 | 113.0825 | 45.3258
283.424 | 280.1028 | 297.0002 | 300.2167 | 279.8167 | 0.013563 | 0.016955 | NoF | 0 | 50.1651 | -189036.5873 | 283.424 | 280.1028 | 0.0031662 | 0.0036226 | 1.4246e-05 | 1.7818e-05 | 0.07939 | 325.088 | 0.025763 | 0.025722 | -0.0016154 | -0.0083946 | -1.125e-06 | -3.3278e-07 | 3.5356e-05 | 0.172% | 0.1583% | 3.7683 | 189.0366 | 0 | 283.424 | 297.0002 | 189.0366 | 50.1651 | ANOVA
282.0679 | 280.4712 | 297.0236 | 298.6849 | 280.3722 | 0.013555 | 0.017002 | NoF | 0 | 36.4886 | -90854.8306 | 282.0679 | 280.4712 | 0.0033401 | 0.0037958 | 1.4269e-05 | 1.7864e-05 | 0.058472 | 261.7815 | 0.02559 | 0.024439 | -6.105e-05 | -0.0033079 | 1.8526e-06 | -3.4448e-06 | 0.00029623 | 0.2881% | 0.1602% | 2.49 | 90.8548 | 0 | 282.0679 | 297.0236 | 90.8548 | 36.4886 |  | df | SS | MS | F | Significance F
283.6647 | 279.9495 | 291.1873 | 294.6703 | 279.8167 | 0.013578 | 0.017005 | NoF | 0 | 46.0997 | -211691.896 | 283.6647 | 279.9495 | 0.0029944 | 0.0031951 | 1.4281e-05 | 1.7858e-05 | 0.072495 | 342.5026 | 0.0031406 | 0.0011456 | -0.0040219 | -0.010766 | -1.0641e-06 | 1.556e-06 | 0.0006173 | 0.1618% | 0.1573% | 4.592 | 211.6919 | 0 | 283.6647 | 291.1873 | 211.6919 | 46.0997 | Regression | 3 | 2551.0079 | 850.336 | 398.52 | 1.347e-20
282.1998 | 280.3885 | 291.2821 | 293.0744 | 280.3722 | 0.013557 | 0.017057 | NoF | 0 | 33.7887 | -103072.0916 | 282.1998 | 280.3885 | 0.0032564 | 0.0034241 | 1.4262e-05 | 1.7917e-05 | 0.053163 | 266.1458 | -0.021899 | -0.022902 | 0.0087609 | 0.0098407 | -2.3078e-06 | -3.707e-06 | 0.00025991 | 0.2582% | 0.1573% | 3.0505 | 103.0721 | 0 | 282.1998 | 291.2821 | 103.0721 | 33.7887 | Residual | 24 | 51.2096 | 2.1337
279.8512 | 277.9211 | 299.8631 | 301.9245 | 277.5944 | 0.013545 | 0.017051 | NoF | 0 | 43.3151 | -109896.1367 | 279.8512 | 277.9211 | 0.0029964 | 0.0030435 | 1.4245e-05 | 1.7906e-05 | 0.068135 | 270.4159 | -0.021765 | -0.025724 | 0.0038509 | 0.005296 | 3.9126e-06 | 1.2763e-06 | 0.00041089 | 0.2461% | 0.1573% | 2.5371 | 109.8961 | 0 | 279.8512 | 299.8631 | 109.8961 | 43.3151 | Total | 27 | 2602.2175
280.7859 | 277.2556 | 293.87 | 297.2818 | 277.0389 | 0.013558 | 0.017025 | NoF | 0 | 49.3107 | -201167.6907 | 280.7859 | 277.2556 | 0.0036778 | 0.0041998 | 1.4275e-05 | 1.7888e-05 | 0.078141 | 338.8024 | -0.0010931 | 0.0032426 | -0.0075909 | -0.010919 | 5.4138e-07 | -1.1563e-06 | 0.00058098 | 0.1684% | 0.1585% | 4.0796 | 201.1677 | 0 | 280.7859 | 293.87 | 201.1677 | 49.3107
279.3957 | 277.6217 | 293.9101 | 295.7896 | 277.5944 | 0.013537 | 0.017081 | NoF | 0 | 36.4974 | -100962.6349 | 279.3957 | 277.6217 | 0.004125 | 0.0043694 | 1.424e-05 | 1.794e-05 | 0.05801 | 266.0068 | -0.0036588 | -0.0028651 | -0.023256 | -0.026536 | -1.2835e-06 | 9.3625e-07 | -0.00068323 | 0.2635% | 0.1589% | 2.7663 | 100.9626 | 0 | 279.3957 | 293.9101 | 100.9626 | 36.4974 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
281.4628 | 277.6535 | 291.4612 | 295.0916 | 277.5944 | 0.013564 | 0.016931 | NoF | 0 | 48.3152 | -217081.5734 | 281.4628 | 277.6535 | 0.003127 | 0.00345 | 1.427e-05 | 1.7783e-05 | 0.076244 | 348.7011 | 0.011977 | 0.015733 | -0.0045294 | -0.010016 | 1.0062e-06 | 6.5532e-07 | 0.00019016 | 0.1606% | 0.1578% | 4.493 | 217.0816 | 0 | 281.4628 | 291.4612 | 217.0816 | 48.3152 | Intercept | -211.8562 | 36.232 | -5.8472 | 4.9668e-06 | -286.6354 | -137.0771 | -286.6354 | -137.0771
279.6371 | 277.6245 | 291.5059 | 293.5774 | 277.5944 | 0.013555 | 0.016975 | NoF | 0 | 36.2696 | -114683.9759 | 279.6371 | 277.6245 | 0.002923 | 0.0029245 | 1.4265e-05 | 1.7835e-05 | 0.057034 | 271.2941 | -0.003026 | -0.0019748 | -0.00080055 | -0.0011631 | -2.1155e-06 | 1.4523e-06 | -0.00092403 | 0.2366% | 0.1572% | 3.162 | 114.684 | 0 | 279.6371 | 291.5059 | 114.684 | 36.2696 | X Variable 1 | -0.31315 | 0.12437 | -2.5179 | 0.018886 | -0.56984 | -0.056463 | -0.56984 | -0.056463
284.6953 | 283.151 | 297.5871 | 299.1621 | 283.15 | 0.013572 | 0.016828 | NoF | 0 | 35.3175 | -87867.6288 | 284.6953 | 283.151 | 0.0030794 | 0.0033672 | 1.4263e-05 | 1.7681e-05 | 0.055818 | 259.8245 | 0.0098959 | 0.01211 | -0.0043738 | -0.010199 | 1.7146e-06 | 4.1779e-07 | -0.00038318 | 0.2957% | 0.158% | 2.4879 | 87.8676 | 0 | 284.6953 | 297.5871 | 87.8676 | 35.3175 | X Variable 2 | 1.0891 | 0.069248 | 15.7274 | 3.8546e-14 | 0.94617 | 1.232 | 0.94617 | 1.232
286.6256 | 283.0832 | 292.2171 | 295.5073 | 283.15 | 0.013598 | 0.016848 | NoF | 0 | 43.9168 | -201837.4757 | 286.6256 | 283.0832 | 0.0029654 | 0.0033459 | 1.4322e-05 | 1.77e-05 | 0.06928 | 338.8019 | 0.003251 | 0.007661 | -0.0017243 | -0.010618 | -3.2597e-06 | -1.0707e-06 | 0.0003182 | 0.1679% | 0.1578% | 4.5959 | 201.8375 | 0 | 286.6256 | 292.2171 | 201.8375 | 43.9168 | X Variable 3 | 0.14587 | 0.0050969 | 28.6192 | 4.6275e-20 | 0.13535 | 0.15639 | 0.13535 | 0.15639
282.4686 | 280.5144 | 302.8174 | 304.8356 | 280.3234 | 0.013565 | 0.016992 | NoF | 0 | 44.989 | -111261.6813 | 282.4686 | 280.5144 | 0.0061578 | 0.0056137 | 1.428e-05 | 1.7845e-05 | 0.075225 | 282.6551 | 0.024223 | 0.022248 | -0.039547 | -0.038558 | 2.7376e-06 | -8.8622e-08 | 0.00073865 | 0.254% | 0.1672% | 2.4731 | 111.2617 | 0 | 282.4686 | 302.8174 | 111.2617 | 44.989
284.7487 | 280.8287 | 297.7124 | 301.4658 | 279.8167 | 0.013586 | 0.016909 | NoF | 0 | 55.5002 | -223371.6162 | 284.7487 | 280.8287 | 0.0029411 | 0.0029788 | 1.4292e-05 | 1.7762e-05 | 0.087281 | 353.0318 | -0.01926 | -0.016018 | -0.00048203 | -0.0029474 | 1.5608e-06 | -1.8828e-06 | -0.00063736 | 0.158% | 0.1573% | 4.0247 | 223.3716 | 0 | 284.7487 | 297.7124 | 223.3716 | 55.5002
283.5443 | 279.8208 | 292.2771 | 295.7757 | 279.8167 | 0.013592 | 0.017201 | NoF | 0 | 47.0492 | -212395.5369 | 283.5443 | 279.8208 | 0.003069 | 0.0035592 | 1.4311e-05 | 1.8082e-05 | 0.074292 | 346.387 | 0.0074662 | 0.0096921 | -0.0030525 | -0.0099182 | -2.2451e-06 | 6.8848e-07 | -0.00012613 | 0.1631% | 0.1579% | 4.5143 | 212.3955 | 0 | 283.5443 | 292.2771 | 212.3955 | 47.0492
282.3742 | 280.4748 | 292.3634 | 294.2605 | 280.3722 | 0.013574 | 0.016947 | NoF | 0 | 34.6895 | -108218.0277 | 282.3742 | 280.4748 | 0.0036097 | 0.0045909 | 1.4272e-05 | 1.78e-05 | 0.056792 | 281.7857 | 0.012665 | 0.015665 | -0.0052137 | -0.007549 | -3.6956e-07 | -4.2743e-07 | 0.00079121 | 0.2604% | 0.1637% | 3.1196 | 108.218 | 0 | 282.3742 | 292.3634 | 108.218 | 34.6895 | RESIDUAL OUTPUT
281.5702 | 278.2284 | 300.3774 | 303.6549 | 277.5944 | 0.013563 | 0.016973 | NoF | 0 | 56.3491 | -190400.1062 | 281.5702 | 278.2284 | 0.002931 | 0.0029343 | 1.4273e-05 | 1.7832e-05 | 0.088651 | 325.2088 | 0.0034655 | 0.0063639 | -0.00061066 | -0.0012452 | -4.3137e-09 | -1.0134e-06 | -0.00050855 | 0.1708% | 0.1573% | 3.3789 | 190.4001 | 0 | 281.5702 | 300.3774 | 190.4001 | 56.3491
279.9294 | 278.002 | 300.1488 | 302.2274 | 277.5944 | 0.013551 | 0.01703 | NoF | 0 | 43.097 | -109778.8685 | 279.9294 | 278.002 | 0.006892 | 0.009437 | 1.424e-05 | 1.7891e-05 | 0.080623 | 305.6336 | 0.026622 | 0.037354 | 0.0029405 | -0.012323 | -1.2431e-06 | -1.6826e-06 | -0.00046632 | 0.2784% | 0.1871% | 2.5472 | 109.7789 | 0 | 279.9294 | 300.1488 | 109.7789 | 43.097 | Observation | Predicted Y | Residuals
280.867 | 277.3397 | 294.2999 | 297.6792 | 277.0389 | 0.013557 | 0.016985 | NoF | 0 | 49.1535 | -200966.6688 | 280.867 | 277.3397 | 0.0037738 | 0.0043456 | 1.4245e-05 | 1.7848e-05 | 0.078065 | 341.7091 | 0.024273 | 0.029359 | -0.0018538 | -0.0073265 | 2.6587e-07 | 3.9186e-08 | 0.0008753 | 0.17% | 0.1588% | 4.0886 | 200.9667 | 0 | 280.867 | 294.2999 | 200.9667 | 49.1535 | 1 | 56.5572 | 0.97657 | [6 empty] | 1.697%
281.5033 | 277.8125 | 291.4421 | 294.9814 | 277.5944 | 0.013561 | 0.016902 | NoF | 0 | 46.5063 | -210266.4282 | 281.5033 | 277.8125 | 0.0041833 | 0.0069492 | 1.4269e-05 | 1.775e-05 | 0.076879 | 422.2507 | -0.019298 | -0.0004562 | -0.012952 | -0.028925 | 4.7237e-07 | 5.4675e-06 | -0.0005212 | 0.2008% | 0.1653% | 4.5212 | 210.2664 | 0 | 281.5033 | 291.4421 | 210.2664 | 46.5063 | 2 | 43.9599 | -1.5566 | [6 empty] | -3.671%
279.5734 | 277.6569 | 291.2495 | 293.2273 | 277.5944 | 0.013548 | 0.01696 | NoF | 0 | 34.9742 | -109153.595 | 279.5734 | 277.6569 | 0.0029118 | 0.0029205 | 1.4171e-05 | 1.7715e-05 | 0.054702 | 266.242 | -0.021602 | -0.021518 | -0.0015053 | -0.0026889 | 1.1826e-06 | -3.9136e-06 | 0.00076985 | 0.2439% | 0.1564% | 3.121 | 109.1536 | 0 | 279.5734 | 291.2495 | 109.1536 | 34.9742 | 3 | 71.9948 | 3.9465 | [6 empty] | 5.197%
[35 empty] | 4 | 35.1075 | -0.0096659 | [6 empty] | -0.02754%
[35 empty] | 5 | 61.0915 | -0.58327 | [6 empty] | -0.964%
[35 empty] | 6 | 44.1472 | -1.6597 | [6 empty] | -3.906%
[35 empty] | 7 | 30.1838 | 2.1139 | [6 empty] | 6.545%
[35 empty] | 8 | 45.8213 | -0.49546 | [6 empty] | -1.093%
[35 empty] | 9 | 50.4228 | -0.2577 | [6 empty] | -0.5137%
[35 empty] | 10 | 36.5512 | -0.062584 | [6 empty] | -0.1715%
[35 empty] | 11 | 47.3214 | -1.2217 | [6 empty] | -2.65%
[35 empty] | 12 | 32.039 | 1.7496 | [6 empty] | 5.178%
[35 empty] | 13 | 43.1154 | 0.19967 | [6 empty] | 0.461%
[35 empty] | 14 | 49.6094 | -0.29876 | [6 empty] | -0.6059%
[35 empty] | 15 | 35.4716 | 1.0258 | [6 empty] | 2.811%
[35 empty] | 16 | 49.0954 | -0.78026 | [6 empty] | -1.615%
[35 empty] | 17 | 34.7791 | 1.4905 | [6 empty] | 4.109%
[35 empty] | 18 | 35.9063 | -0.58886 | [6 empty] | -1.667%
[35 empty] | 19 | 46.0782 | -2.1614 | [6 empty] | -4.922%
[35 empty] | 20 | 45.7124 | -0.72338 | [6 empty] | -1.608%
[35 empty] | 21 | 55.792 | -0.2918 | [6 empty] | -0.5258%
[35 empty] | 22 | 48.6486 | -1.5994 | [6 empty] | -3.399%
[35 empty] | 23 | 33.9127 | 0.77674 | [6 empty] | 2.239%
[35 empty] | 24 | 54.8803 | 1.4689 | [6 empty] | 2.607%
[35 empty] | 25 | 43.385 | -0.28794 | [6 empty] | -0.6681%
[35 empty] | 26 | 50.0228 | -0.86932 | [6 empty] | -1.769%
[35 empty] | 27 | 48.0678 | -1.5615 | [6 empty] | -3.358%
[35 empty] | 28 | 33.7131 | 1.2611 | [6 empty] | 3.606%

## test_file_00 (2)
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level | TEO_K_mean | TCI_K_mean | Cooling capacity [kW] | Q^2 | TEO*Q | TCI*Q | kW_mean | SUMMARY OUTPUT | [9 empty] | Intercept | X Variable 1 | X Variable 2 | X Variable 3 | X Variable 4 | X Variable 5 | X Variable 6
287.0211 | 283.5728 | 302.7232 | 305.9926 | 283.15 | 0.013574 | 0.01687 | NoF | 0 | 57.5337 | -196083.8885 | 287.0211 | 283.5728 | 0.0035352 | 0.0032638 | 1.4289e-05 | 1.7738e-05 | 0.090939 | 331.1712 | 0.0081956 | 0.0070162 | 0.012345 | 0.012525 | 6.9955e-07 | -2.4459e-06 | 0.00080527 | 0.1689% | 0.1581% | 3.4082 | 196.0839 | 0 | 283.5728 | 302.7232 | 196.0839 | 38448.8913 | 55604.0517 | 59359.142 | 57.5337 | [10 empty] | 35.6831 | -0.37658 | 0.32564 | -1.2913 | 0.00012563 | -0.00053401 | 0.0051885
285.1628 | 283.2962 | 302.6607 | 304.5239 | 283.15 | 0.013574 | 0.016943 | NoF | 0 | 42.4033 | -106201.144 | 285.1628 | 283.2962 | 0.0034386 | 0.0042815 | 1.4276e-05 | 1.7799e-05 | 0.068925 | 280.7022 | 0.013549 | 0.019668 | -0.0016335 | -0.01023 | 1.205e-07 | -5.9568e-07 | 0.00085124 | 0.2643% | 0.1625% | 2.5045 | 106.2011 | 0 | 283.2962 | 302.6607 | 106.2011 | 11278.683 | 30086.3821 | 32142.9109 | 42.4033 | Regression Statistics
289.3396 | 283.2563 | 297.3904 | 303.1459 | 282.5944 | 0.013614 | 0.016704 | NoF | 0 | 75.9413 | -346708.8515 | 289.3396 | 283.2563 | 0.0031795 | 0.0034681 | 1.4313e-05 | 1.7548e-05 | 0.11968 | 475.8415 | -0.025143 | -0.031243 | -0.0098445 | -0.005959 | 7.6866e-07 | 1.0574e-06 | 0.00058385 | 0.1372% | 0.1576% | 4.5655 | 346.7089 | 0 | 283.2563 | 297.3904 | 346.7089 | 120207.0277 | 98207.4835 | 103107.8681 | 75.9413 | Multiple R | 0.99922
284.9085 | 283.3896 | 297.1093 | 298.6959 | 283.15 | 0.013572 | 0.01683 | NoF | 0 | 35.0978 | -86416.0624 | 284.9085 | 283.3896 | 0.004789 | 0.0056103 | 1.4275e-05 | 1.7684e-05 | 0.060402 | 273.6682 | 0.0016149 | 0.00010352 | -0.010847 | -0.01864 | 1.3926e-06 | 1.1925e-06 | -7.1667e-05 | 0.3167% | 0.1721% | 2.4622 | 86.4161 | 0 | 283.3896 | 297.1093 | 86.4161 | 7467.7358 | 24489.4152 | 25675.0141 | 35.0978 | R Square | 0.99843
288.2445 | 283.1384 | 294.5706 | 299.32 | 282.5944 | 0.013593 | 0.016774 | NoF | 0 | 60.5082 | -290664.1768 | 288.2445 | 283.1384 | 0.00301 | 0.0030414 | 1.43e-05 | 1.7618e-05 | 0.095309 | 415.0542 | -0.015969 | -0.015078 | -0.0053639 | -0.0040643 | 3.1229e-07 | 1.6398e-06 | -0.00075872 | 0.1428% | 0.1575% | 4.8037 | 290.6642 | 0 | 283.1384 | 294.5706 | 290.6642 | 84485.6637 | 82298.1901 | 85621.1134 | 60.5082 | Adjusted R Square | 0.99798
286.4847 | 283.1062 | 291.6634 | 294.7821 | 283.15 | 0.013593 | 0.016907 | NoF | 0 | 42.4875 | -192431.2297 | 286.4847 | 283.1062 | 0.0029399 | 0.0030077 | 1.4289e-05 | 1.7756e-05 | 0.066811 | 326.2953 | -0.00059457 | -0.00031003 | -0.00044381 | -0.0050624 | -2.8793e-06 | 1.6091e-06 | -0.00085332 | 0.1696% | 0.1572% | 4.5291 | 192.4312 | 0 | 283.1062 | 291.6634 | 192.4312 | 37029.7782 | 54478.4677 | 56125.1409 | 42.4875 | Standard Error | 0.44084
285.116 | 283.2578 | 290.0515 | 291.8041 | 283.15 | 0.013583 | 0.017029 | NoF | 0 | 32.2977 | -105801.7462 | 285.116 | 283.2578 | 0.0030693 | 0.0034222 | 1.428e-05 | 1.7882e-05 | 0.052047 | 275.889 | 0.015505 | 0.018688 | 0.0019594 | -0.0016754 | 2.1981e-06 | 2.1522e-07 | -0.0007377 | 0.2608% | 0.1611% | 3.2758 | 105.8017 | 0 | 283.2578 | 290.0515 | 105.8017 | 11194.0095 | 29969.1649 | 30687.958 | 32.2977 | Observations | 28
282.5718 | 280.5848 | 302.7032 | 304.748 | 280.3722 | 0.01356 | 0.01697 | NoF | 0 | 45.3258 | -113082.5014 | 282.5718 | 280.5848 | 0.0030708 | 0.0030267 | 1.4278e-05 | 1.7837e-05 | 0.071285 | 270.0064 | -0.011196 | -0.011273 | 0.0055513 | 0.0027987 | 8.3799e-07 | 3.5991e-07 | -0.00054181 | 0.2388% | 0.1573% | 2.4949 | 113.0825 | 0 | 280.5848 | 302.7032 | 113.0825 | 12787.6521 | 31729.2309 | 34230.4322 | 45.3258
283.424 | 280.1028 | 297.0002 | 300.2167 | 279.8167 | 0.013563 | 0.016955 | NoF | 0 | 50.1651 | -189036.5873 | 283.424 | 280.1028 | 0.0031662 | 0.0036226 | 1.4246e-05 | 1.7818e-05 | 0.07939 | 325.088 | 0.025763 | 0.025722 | -0.0016154 | -0.0083946 | -1.125e-06 | -3.3278e-07 | 3.5356e-05 | 0.172% | 0.1583% | 3.7683 | 189.0366 | 0 | 280.1028 | 297.0002 | 189.0366 | 35734.8313 | 52949.679 | 56143.9011 | 50.1651 | ANOVA
282.0679 | 280.4712 | 297.0236 | 298.6849 | 280.3722 | 0.013555 | 0.017002 | NoF | 0 | 36.4886 | -90854.8306 | 282.0679 | 280.4712 | 0.0033401 | 0.0037958 | 1.4269e-05 | 1.7864e-05 | 0.058472 | 261.7815 | 0.02559 | 0.024439 | -6.105e-05 | -0.0033079 | 1.8526e-06 | -3.4448e-06 | 0.00029623 | 0.2881% | 0.1602% | 2.49 | 90.8548 | 0 | 280.4712 | 297.0236 | 90.8548 | 8254.6002 | 25482.1619 | 26986.0257 | 36.4886 |  | df | SS | MS | F | Significance F
283.6647 | 279.9495 | 291.1873 | 294.6703 | 279.8167 | 0.013578 | 0.017005 | NoF | 0 | 46.0997 | -211691.896 | 283.6647 | 279.9495 | 0.0029944 | 0.0031951 | 1.4281e-05 | 1.7858e-05 | 0.072495 | 342.5026 | 0.0031406 | 0.0011456 | -0.0040219 | -0.010766 | -1.0641e-06 | 1.556e-06 | 0.0006173 | 0.1618% | 0.1573% | 4.592 | 211.6919 | 0 | 279.9495 | 291.1873 | 211.6919 | 44813.4588 | 59263.03 | 61641.992 | 46.0997 | Regression | 6 | 2598.1365 | 433.0227 | 2228.205 | 2.5548e-28
282.1998 | 280.3885 | 291.2821 | 293.0744 | 280.3722 | 0.013557 | 0.017057 | NoF | 0 | 33.7887 | -103072.0916 | 282.1998 | 280.3885 | 0.0032564 | 0.0034241 | 1.4262e-05 | 1.7917e-05 | 0.053163 | 266.1458 | -0.021899 | -0.022902 | 0.0087609 | 0.0098407 | -2.3078e-06 | -3.707e-06 | 0.00025991 | 0.2582% | 0.1573% | 3.0505 | 103.0721 | 0 | 280.3885 | 291.2821 | 103.0721 | 10623.8561 | 28900.2315 | 30023.0566 | 33.7887 | Residual | 21 | 4.0811 | 0.19434
279.8512 | 277.9211 | 299.8631 | 301.9245 | 277.5944 | 0.013545 | 0.017051 | NoF | 0 | 43.3151 | -109896.1367 | 279.8512 | 277.9211 | 0.0029964 | 0.0030435 | 1.4245e-05 | 1.7906e-05 | 0.068135 | 270.4159 | -0.021765 | -0.025724 | 0.0038509 | 0.005296 | 3.9126e-06 | 1.2763e-06 | 0.00041089 | 0.2461% | 0.1573% | 2.5371 | 109.8961 | 0 | 277.9211 | 299.8631 | 109.8961 | 12077.1609 | 30542.451 | 32953.7991 | 43.3151 | Total | 27 | 2602.2175
280.7859 | 277.2556 | 293.87 | 297.2818 | 277.0389 | 0.013558 | 0.017025 | NoF | 0 | 49.3107 | -201167.6907 | 280.7859 | 277.2556 | 0.0036778 | 0.0041998 | 1.4275e-05 | 1.7888e-05 | 0.078141 | 338.8024 | -0.0010931 | 0.0032426 | -0.0075909 | -0.010919 | 5.4138e-07 | -1.1563e-06 | 0.00058098 | 0.1684% | 0.1585% | 4.0796 | 201.1677 | 0 | 277.2556 | 293.87 | 201.1677 | 40468.4398 | 55774.8599 | 59117.1542 | 49.3107
279.3957 | 277.6217 | 293.9101 | 295.7896 | 277.5944 | 0.013537 | 0.017081 | NoF | 0 | 36.4974 | -100962.6349 | 279.3957 | 277.6217 | 0.004125 | 0.0043694 | 1.424e-05 | 1.794e-05 | 0.05801 | 266.0068 | -0.0036588 | -0.0028651 | -0.023256 | -0.026536 | -1.2835e-06 | 9.3625e-07 | -0.00068323 | 0.2635% | 0.1589% | 2.7663 | 100.9626 | 0 | 277.6217 | 293.9101 | 100.9626 | 10193.4536 | 28029.4156 | 29673.9416 | 36.4974 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
281.4628 | 277.6535 | 291.4612 | 295.0916 | 277.5944 | 0.013564 | 0.016931 | NoF | 0 | 48.3152 | -217081.5734 | 281.4628 | 277.6535 | 0.003127 | 0.00345 | 1.427e-05 | 1.7783e-05 | 0.076244 | 348.7011 | 0.011977 | 0.015733 | -0.0045294 | -0.010016 | 1.0062e-06 | 6.5532e-07 | 0.00019016 | 0.1606% | 0.1578% | 4.493 | 217.0816 | 0 | 277.6535 | 291.4612 | 217.0816 | 47124.4095 | 60273.4543 | 63270.8631 | 48.3152 | Intercept | 35.6831 | 34.2299 | 1.0425 | 0.30905 | -35.5018 | 106.868 | -35.5018 | 106.868
279.6371 | 277.6245 | 291.5059 | 293.5774 | 277.5944 | 0.013555 | 0.016975 | NoF | 0 | 36.2696 | -114683.9759 | 279.6371 | 277.6245 | 0.002923 | 0.0029245 | 1.4265e-05 | 1.7835e-05 | 0.057034 | 271.2941 | -0.003026 | -0.0019748 | -0.00080055 | -0.0011631 | -2.1155e-06 | 1.4523e-06 | -0.00092403 | 0.2366% | 0.1572% | 3.162 | 114.684 | 0 | 277.6245 | 291.5059 | 114.684 | 13152.4143 | 31839.0863 | 33431.0581 | 36.2696 | X Variable 1 | -0.37658 | 0.11762 | -3.2017 | 0.0042863 | -0.62118 | -0.13198 | -0.62118 | -0.13198
284.6953 | 283.151 | 297.5871 | 299.1621 | 283.15 | 0.013572 | 0.016828 | NoF | 0 | 35.3175 | -87867.6288 | 284.6953 | 283.151 | 0.0030794 | 0.0033672 | 1.4263e-05 | 1.7681e-05 | 0.055818 | 259.8245 | 0.0098959 | 0.01211 | -0.0043738 | -0.010199 | 1.7146e-06 | 4.1779e-07 | -0.00038318 | 0.2957% | 0.158% | 2.4879 | 87.8676 | 0 | 283.151 | 297.5871 | 87.8676 | 7720.7202 | 24879.8049 | 26148.2691 | 35.3175 | X Variable 2 | 0.32564 | 0.068495 | 4.7542 | 0.0001073 | 0.1832 | 0.46809 | 0.1832 | 0.46809
286.6256 | 283.0832 | 292.2171 | 295.5073 | 283.15 | 0.013598 | 0.016848 | NoF | 0 | 43.9168 | -201837.4757 | 286.6256 | 283.0832 | 0.0029654 | 0.0033459 | 1.4322e-05 | 1.77e-05 | 0.06928 | 338.8019 | 0.003251 | 0.007661 | -0.0017243 | -0.010618 | -3.2597e-06 | -1.0707e-06 | 0.0003182 | 0.1679% | 0.1578% | 4.5959 | 201.8375 | 0 | 283.0832 | 292.2171 | 201.8375 | 40738.3666 | 57136.7884 | 58980.3606 | 43.9168 | X Variable 3 | -1.2913 | 0.21082 | -6.1249 | 4.4582e-06 | -1.7297 | -0.85283 | -1.7297 | -0.85283
282.4686 | 280.5144 | 302.8174 | 304.8356 | 280.3234 | 0.013565 | 0.016992 | NoF | 0 | 44.989 | -111261.6813 | 282.4686 | 280.5144 | 0.0061578 | 0.0056137 | 1.428e-05 | 1.7845e-05 | 0.075225 | 282.6551 | 0.024223 | 0.022248 | -0.039547 | -0.038558 | 2.7376e-06 | -8.8622e-08 | 0.00073865 | 0.254% | 0.1672% | 2.4731 | 111.2617 | 0 | 280.5144 | 302.8174 | 111.2617 | 12379.1617 | 31210.5046 | 33691.973 | 44.989 | X Variable 4 | 0.00012563 | 2.0526e-05 | 6.1206 | 4.5024e-06 | 8.2944e-05 | 0.00016831 | 8.2944e-05 | 0.00016831
284.7487 | 280.8287 | 297.7124 | 301.4658 | 279.8167 | 0.013586 | 0.016909 | NoF | 0 | 55.5002 | -223371.6162 | 284.7487 | 280.8287 | 0.0029411 | 0.0029788 | 1.4292e-05 | 1.7762e-05 | 0.087281 | 353.0318 | -0.01926 | -0.016018 | -0.00048203 | -0.0029474 | 1.5608e-06 | -1.8828e-06 | -0.00063736 | 0.158% | 0.1573% | 4.0247 | 223.3716 | 0 | 280.8287 | 297.7124 | 223.3716 | 49894.8789 | 62729.1591 | 66500.4984 | 55.5002 | X Variable 5 | -0.00053401 | 0.00073651 | -0.72505 | 0.47642 | -0.0020657 | 0.00099765 | -0.0020657 | 0.00099765
283.5443 | 279.8208 | 292.2771 | 295.7757 | 279.8167 | 0.013592 | 0.017201 | NoF | 0 | 47.0492 | -212395.5369 | 283.5443 | 279.8208 | 0.003069 | 0.0035592 | 1.4311e-05 | 1.8082e-05 | 0.074292 | 346.387 | 0.0074662 | 0.0096921 | -0.0030525 | -0.0099182 | -2.2451e-06 | 6.8848e-07 | -0.00012613 | 0.1631% | 0.1579% | 4.5143 | 212.3955 | 0 | 279.8208 | 292.2771 | 212.3955 | 45111.8641 | 59432.6799 | 62078.3529 | 47.0492 | X Variable 6 | 0.0051885 | 0.00045745 | 11.3421 | 2.0449e-10 | 0.0042372 | 0.0061398 | 0.0042372 | 0.0061398
282.3742 | 280.4748 | 292.3634 | 294.2605 | 280.3722 | 0.013574 | 0.016947 | NoF | 0 | 34.6895 | -108218.0277 | 282.3742 | 280.4748 | 0.0036097 | 0.0045909 | 1.4272e-05 | 1.78e-05 | 0.056792 | 281.7857 | 0.012665 | 0.015665 | -0.0052137 | -0.007549 | -3.6956e-07 | -4.2743e-07 | 0.00079121 | 0.2604% | 0.1637% | 3.1196 | 108.218 | 0 | 280.4748 | 292.3634 | 108.218 | 11711.1415 | 30352.4282 | 31638.9939 | 34.6895
281.5702 | 278.2284 | 300.3774 | 303.6549 | 277.5944 | 0.013563 | 0.016973 | NoF | 0 | 56.3491 | -190400.1062 | 281.5702 | 278.2284 | 0.002931 | 0.0029343 | 1.4273e-05 | 1.7832e-05 | 0.088651 | 325.2088 | 0.0034655 | 0.0063639 | -0.00061066 | -0.0012452 | -4.3137e-09 | -1.0134e-06 | -0.00050855 | 0.1708% | 0.1573% | 3.3789 | 190.4001 | 0 | 278.2284 | 300.3774 | 190.4001 | 36252.2005 | 52974.7263 | 57191.8911 | 56.3491
279.9294 | 278.002 | 300.1488 | 302.2274 | 277.5944 | 0.013551 | 0.01703 | NoF | 0 | 43.097 | -109778.8685 | 279.9294 | 278.002 | 0.006892 | 0.009437 | 1.424e-05 | 1.7891e-05 | 0.080623 | 305.6336 | 0.026622 | 0.037354 | 0.0029405 | -0.012323 | -1.2431e-06 | -1.6826e-06 | -0.00046632 | 0.2784% | 0.1871% | 2.5472 | 109.7789 | 0 | 278.002 | 300.1488 | 109.7789 | 12051.4 | 30518.7399 | 32950.0001 | 43.097
280.867 | 277.3397 | 294.2999 | 297.6792 | 277.0389 | 0.013557 | 0.016985 | NoF | 0 | 49.1535 | -200966.6688 | 280.867 | 277.3397 | 0.0037738 | 0.0043456 | 1.4245e-05 | 1.7848e-05 | 0.078065 | 341.7091 | 0.024273 | 0.029359 | -0.0018538 | -0.0073265 | 2.6587e-07 | 3.9186e-08 | 0.0008753 | 0.17% | 0.1588% | 4.0886 | 200.9667 | 0 | 277.3397 | 294.2999 | 200.9667 | 40387.602 | 55736.0444 | 59144.4661 | 49.1535 | RESIDUAL OUTPUT
281.5033 | 277.8125 | 291.4421 | 294.9814 | 277.5944 | 0.013561 | 0.016902 | NoF | 0 | 46.5063 | -210266.4282 | 281.5033 | 277.8125 | 0.0041833 | 0.0069492 | 1.4269e-05 | 1.775e-05 | 0.076879 | 422.2507 | -0.019298 | -0.0004562 | -0.012952 | -0.028925 | 4.7237e-07 | 5.4675e-06 | -0.0005212 | 0.2008% | 0.1653% | 4.5212 | 210.2664 | 0 | 277.8125 | 291.4421 | 210.2664 | 44211.9708 | 58414.6453 | 61280.4945 | 46.5063
279.5734 | 277.6569 | 291.2495 | 293.2273 | 277.5944 | 0.013548 | 0.01696 | NoF | 0 | 34.9742 | -109153.595 | 279.5734 | 277.6569 | 0.0029118 | 0.0029205 | 1.4171e-05 | 1.7715e-05 | 0.054702 | 266.242 | -0.021602 | -0.021518 | -0.0015053 | -0.0026889 | 1.1826e-06 | -3.9136e-06 | 0.00076985 | 0.2439% | 0.1564% | 3.121 | 109.1536 | 0 | 277.6569 | 291.2495 | 109.1536 | 11914.5073 | 30307.2537 | 31790.9318 | 34.9742 | Observation | Predicted Y | Residuals
[38 empty] | 1 | 57.4021 | 0.13167 | [6 empty] | 0.2289%
[38 empty] | 2 | 42.5499 | -0.14656 | [6 empty] | -0.3456%
[38 empty] | 3 | 75.7993 | 0.14201 | [6 empty] | 0.187%
[38 empty] | 4 | 35.206 | -0.1082 | [6 empty] | -0.3083%
[38 empty] | 5 | 60.5718 | -0.0636 | [6 empty] | -0.1051%
[38 empty] | 6 | 42.336 | 0.15151 | [6 empty] | 0.3566%
[38 empty] | 7 | 31.4769 | 0.82076 | [6 empty] | 2.541%
[38 empty] | 8 | 44.8425 | 0.48333 | [6 empty] | 1.066%
[38 empty] | 9 | 50.3393 | -0.1742 | [6 empty] | -0.3473%
[38 empty] | 10 | 36.9164 | -0.42783 | [6 empty] | -1.173%
[38 empty] | 11 | 45.5462 | 0.5535 | [6 empty] | 1.201%
[38 empty] | 12 | 33.5322 | 0.25648 | [6 empty] | 0.7591%
[38 empty] | 13 | 42.9559 | 0.35918 | [6 empty] | 0.8292%
[38 empty] | 14 | 49.2405 | 0.070189 | [6 empty] | 0.1423%
[38 empty] | 15 | 36.7534 | -0.25599 | [6 empty] | -0.7014%
[38 empty] | 16 | 47.7427 | 0.57251 | [6 empty] | 1.185%
[38 empty] | 17 | 36.0827 | 0.1869 | [6 empty] | 0.5153%
[38 empty] | 18 | 35.8559 | -0.53843 | [6 empty] | -1.525%
[38 empty] | 19 | 44.2397 | -0.32286 | [6 empty] | -0.7352%
[38 empty] | 20 | 44.6892 | 0.29977 | [6 empty] | 0.6663%
[38 empty] | 21 | 56.2541 | -0.75391 | [6 empty] | -1.358%
[38 empty] | 22 | 47.2519 | -0.20266 | [6 empty] | -0.4307%
[38 empty] | 23 | 34.9525 | -0.26304 | [6 empty] | -0.7583%
[38 empty] | 24 | 55.8733 | 0.4758 | [6 empty] | 0.8444%
[38 empty] | 25 | 43.1596 | -0.062557 | [6 empty] | -0.1452%
[38 empty] | 26 | 49.7606 | -0.60708 | [6 empty] | -1.235%
[38 empty] | 27 | 46.7764 | -0.27012 | [6 empty] | -0.5808%
[38 empty] | 28 | 35.2808 | -0.30659 | [6 empty] | -0.8766%

## test_file_UC
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level | TEO_K_mean | TCI_K_mean | Cooling capacity [kW] | Q^2 | TEO*Q | TCI*Q | kW_mean | kW_NF | kW/kW_NF
289.4975 | 283.9184 | 303.1569 | 308.4018 | 282.625 | 0.013616 | 0.016838 | UC | 10 | 83.3485 | -317967.5902 | 289.4975 | 283.9184 | 0.0039671 | 0.0037398 | 1.4322e-05 | 1.7695e-05 | 0.13672 | 445.1566 | -0.0047274 | -0.0063556 | 0.01599 | 0.018799 | -1.2118e-07 | -2.2258e-06 | -0.00040612 | 0.14% | 0.164% | 3.8149 | 317.9676 | -10 | 283.9184 | 303.1569 | 317.9676 | 101103.3884 | 90276.8613 | 96394.0685 | 83.3485 | 81.5408 | 1.0222
285.2089 | 283.3288 | 302.9882 | 304.8701 | 283.15 | 0.013595 | 0.01704 | UC | 10 | 43.1821 | -107136.5349 | 285.2089 | 283.3288 | 0.0031586 | 0.0032765 | 1.4297e-05 | 1.7894e-05 | 0.068641 | 269.5138 | -0.027852 | -0.030164 | -0.0065713 | -0.0046784 | 1.5854e-06 | -1.8472e-06 | 0.0009102 | 0.2516% | 0.159% | 2.481 | 107.1365 | -10 | 283.3288 | 302.9882 | 107.1365 | 11478.2371 | 30354.8675 | 32461.1077 | 43.1821 | 42.9691 | 1.005
288.9947 | 283.2889 | 297.3038 | 302.665 | 282.5944 | 0.013627 | 0.016787 | UC | 10 | 70.8889 | -325543.3168 | 288.9947 | 283.2889 | 0.0032194 | 0.0033331 | 1.434e-05 | 1.7637e-05 | 0.11166 | 451.5501 | -0.024157 | -0.026683 | -0.011075 | -0.0094415 | 5.972e-08 | 1.6929e-06 | 0.0006926 | 0.1387% | 0.1575% | 4.5923 | 325.5433 | -10 | 283.2889 | 297.3038 | 325.5433 | 105978.4511 | 92222.8244 | 96785.2603 | 70.8889 | 71.6926 | 0.98879
286.8985 | 283.2828 | 297.5716 | 300.9607 | 283.15 | 0.013603 | 0.0169 | UC | 10 | 51.4691 | -206059.9088 | 286.8985 | 283.2828 | 0.002988 | 0.0030083 | 1.4314e-05 | 1.7759e-05 | 0.080946 | 338.7134 | -0.021158 | -0.019527 | -0.00065191 | -0.0016436 | -7.5781e-07 | -1.3426e-06 | 0.00086765 | 0.1644% | 0.1573% | 4.0036 | 206.0599 | -10 | 283.2828 | 297.5716 | 206.0599 | 42460.686 | 58373.2372 | 61317.5666 | 51.4691 | 52.1385 | 0.98716
284.8264 | 283.2868 | 297.4267 | 298.9828 | 283.15 | 0.013587 | 0.016899 | UC | 10 | 35.3724 | -87691.0759 | 284.8264 | 283.2868 | 0.0035057 | 0.0038687 | 1.4292e-05 | 1.7776e-05 | 0.057261 | 267.207 | 0.026127 | 0.028302 | 0.0050783 | 0.0044859 | -1.6808e-06 | -7.5913e-06 | 0.00025323 | 0.3047% | 0.1619% | 2.4791 | 87.6911 | -10 | 283.2868 | 297.4267 | 87.6911 | 7689.7248 | 24841.7254 | 26081.6708 | 35.3724 | 35.6514 | 0.99217
286.5147 | 283.1143 | 291.783 | 294.9455 | 283.15 | 0.01362 | 0.016956 | UC | 10 | 42.8795 | -194059.4391 | 286.5147 | 283.1143 | 0.0030944 | 0.0032147 | 1.4317e-05 | 1.7808e-05 | 0.067759 | 331.453 | -0.014477 | -0.01847 | -0.0065488 | -0.010947 | -1.899e-06 | -6.5713e-08 | 0.0002322 | 0.1708% | 0.158% | 4.5257 | 194.0594 | -10 | 283.1143 | 291.783 | 194.0594 | 37659.0659 | 54940.9995 | 56623.2389 | 42.8795 | 42.6859 | 1.0045
285.1974 | 283.1156 | 290.7062 | 292.6385 | 283.15 | 0.013606 | 0.017084 | UC | 10 | 34.0088 | -118729.4647 | 285.1974 | 283.1156 | 0.003342 | 0.0040682 | 1.4305e-05 | 1.7946e-05 | 0.05364 | 280.5376 | 0.0060307 | 0.010062 | -0.0087694 | -0.017064 | -1.717e-06 | -1.8749e-07 | 0.00028189 | 0.2363% | 0.1577% | 3.4911 | 118.7295 | -10 | 283.1156 | 290.7062 | 118.7295 | 14096.6858 | 33614.1598 | 34515.3875 | 34.0088 | 33.3274 | 1.0204
283.9981 | 280.522 | 303.1947 | 306.5783 | 280.3722 | 0.013603 | 0.016995 | UC | 10 | 61.4275 | -198371.3254 | 283.9981 | 280.522 | 0.0029459 | 0.0029508 | 1.4297e-05 | 1.7866e-05 | 0.096627 | 331.3027 | -0.017292 | -0.016975 | -0.0010363 | -0.0021744 | 1.6277e-07 | -1.3504e-06 | -0.00075394 | 0.167% | 0.1573% | 3.2294 | 198.3713 | -10 | 280.522 | 303.1947 | 198.3713 | 39351.1827 | 55647.5287 | 60145.1322 | 61.4275 | 59.919 | 1.0252
282.4005 | 280.3766 | 303.0301 | 305.1209 | 280.3722 | 0.013589 | 0.017071 | UC | 10 | 46.2127 | -115438.4903 | 282.4005 | 280.3766 | 0.0039338 | 0.0048828 | 1.4286e-05 | 1.7931e-05 | 0.074707 | 280.3336 | -0.01607 | -0.010394 | 0.0011987 | -0.0043521 | 1.2299e-07 | 5.4439e-07 | 0.0001806 | 0.2428% | 0.1617% | 2.498 | 115.4385 | -10 | 280.3766 | 303.0301 | 115.4385 | 13326.045 | 32366.2535 | 34981.337 | 46.2127 | 45.6087 | 1.0132
282.2467 | 280.6029 | 297.3809 | 299.0628 | 280.3539 | 0.013602 | 0.017048 | UC | 10 | 37.0049 | -93852.0524 | 282.2467 | 280.6029 | 0.0030063 | 0.0029568 | 1.4302e-05 | 1.7909e-05 | 0.058394 | 260.2749 | 0.00082603 | 0.00046133 | -0.0064899 | -0.0045464 | 2.0154e-06 | -8.2111e-07 | 0.00058098 | 0.2773% | 0.1578% | 2.5362 | 93.8521 | -10 | 280.6029 | 297.3809 | 93.8521 | 8808.2077 | 26335.1552 | 27909.807 | 37.0049 | 37.5201 | 0.98627
281.1733 | 277.3523 | 295.0471 | 298.6892 | 277.0389 | 0.013562 | 0.01706 | UC | 10 | 52.791 | -217754.7791 | 281.1733 | 277.3523 | 0.0029377 | 0.0029377 | 1.4262e-05 | 1.7931e-05 | 0.083019 | 347.6568 | -0.00073897 | -0.0011127 | 0.002287 | 0.0025885 | -8.5004e-08 | 1.3468e-06 | -0.00049594 | 0.1597% | 0.1573% | 4.1248 | 217.7548 | -10 | 277.3523 | 295.0471 | 217.7548 | 47417.1438 | 60394.7932 | 64247.9228 | 52.791 | 53.1959 | 0.99239
279.5859 | 277.5354 | 292.0719 | 294.1836 | 277.5944 | 0.013575 | 0.01704 | UC | 10 | 36.3995 | -117023.5435 | 279.5859 | 277.5354 | 0.0029325 | 0.0029359 | 1.4286e-05 | 1.79e-05 | 0.057242 | 272.6495 | 0.00041886 | 0.00011254 | -0.001074 | -0.002149 | 1.269e-06 | -2.4211e-06 | -0.00097563 | 0.233% | 0.1573% | 3.215 | 117.0235 | -10 | 277.5354 | 292.0719 | 117.0235 | 13694.5097 | 32478.177 | 34179.2835 | 36.3995 | 36.8885 | 0.98674
289.4874 | 283.792 | 303.3427 | 308.7384 | 282.5944 | 0.013612 | 0.016817 | UC | 20 | 85.1125 | -324502.4336 | 289.4874 | 283.792 | 0.0029202 | 0.0030017 | 1.4324e-05 | 1.7666e-05 | 0.13394 | 448.9747 | -0.0027775 | -0.0033158 | 0.00019961 | 0.0023247 | 1.925e-06 | -1.3384e-07 | 0.00034018 | 0.1384% | 0.1574% | 3.8126 | 324.5024 | -20 | 283.792 | 303.3427 | 324.5024 | 105301.8294 | 92091.1954 | 98435.4557 | 85.1125 | 83.361 | 1.021
285.0077 | 283.1159 | 303.1122 | 305.0083 | 283.15 | 0.013579 | 0.017007 | UC | 20 | 43.2727 | -107681.0161 | 285.0077 | 283.1159 | 0.0029448 | 0.0029518 | 1.4367e-05 | 1.7964e-05 | 0.068426 | 268.5414 | -0.002635 | -0.0021449 | -1.0294e-05 | -0.00098898 | 7.0632e-07 | 9.3217e-08 | -0.00028063 | 0.2494% | 0.1581% | 2.4884 | 107.681 | -20 | 283.1159 | 303.1122 | 107.681 | 11595.2012 | 30486.2106 | 32639.4321 | 43.2727 | 43.2563 | 1.0004
286.838 | 283.1972 | 297.7759 | 301.2312 | 283.15 | 0.013597 | 0.016827 | UC | 20 | 51.7273 | -207410.8772 | 286.838 | 283.1972 | 0.0029632 | 0.0029555 | 1.4378e-05 | 1.7791e-05 | 0.081797 | 340.823 | -0.00040712 | -0.00024306 | -0.00015811 | 0.0002093 | 1.5172e-06 | -7.3377e-06 | 0.00079125 | 0.1643% | 0.1581% | 4.0097 | 207.4109 | -20 | 283.1972 | 297.7759 | 207.4109 | 43019.272 | 58738.1715 | 61761.966 | 51.7273 | 52.674 | 0.98203
284.3436 | 280.8416 | 303.2966 | 306.6873 | 280.3722 | 0.013578 | 0.016955 | UC | 20 | 61.2355 | -199460.1589 | 284.3436 | 280.8416 | 0.0029732 | 0.0030286 | 1.4294e-05 | 1.7829e-05 | 0.096425 | 332.6248 | -0.029103 | -0.028444 | 0.0019175 | 0.003517 | 1.3528e-06 | -2.1553e-06 | 0.00081414 | 0.1668% | 0.1575% | 3.2573 | 199.4602 | -20 | 280.8416 | 303.2966 | 199.4602 | 39784.355 | 56016.7174 | 60495.5843 | 61.2355 | 60.1015 | 1.0189
282.2209 | 280.5353 | 297.4835 | 299.1611 | 280.3722 | 0.013574 | 0.017038 | UC | 20 | 37.2756 | -96045.1982 | 282.2209 | 280.5353 | 0.0030596 | 0.0030584 | 1.428e-05 | 1.791e-05 | 0.058617 | 261.4417 | -0.0039014 | -0.0045204 | 0.0056182 | 0.0053087 | -3.9126e-07 | 5.7996e-07 | 0.00069661 | 0.2722% | 0.1573% | 2.5766 | 96.0452 | -20 | 280.5353 | 297.4835 | 96.0452 | 9224.6801 | 26944.0672 | 28571.8633 | 37.2756 | 37.9092 | 0.98329
282.5093 | 280.5132 | 292.3178 | 294.3062 | 280.3722 | 0.01357 | 0.017076 | UC | 20 | 35.6096 | -113690.8423 | 282.5093 | 280.5132 | 0.0031067 | 0.0031998 | 1.4272e-05 | 1.793e-05 | 0.056534 | 280.7794 | -0.031785 | -0.03639 | -0.0062446 | -0.00448 | 3.4002e-07 | -2.5911e-06 | -0.00045772 | 0.247% | 0.1588% | 3.1927 | 113.6908 | -20 | 280.5132 | 292.3178 | 113.6908 | 12925.6076 | 31891.7874 | 33233.853 | 35.6096 | 35.4618 | 1.0042
281.2636 | 277.8284 | 300.124 | 303.4798 | 277.6555 | 0.013538 | 0.017018 | UC | 20 | 56.0434 | -195400.0188 | 281.2636 | 277.8284 | 0.003099 | 0.0035771 | 1.424e-05 | 1.7879e-05 | 0.088448 | 336.3175 | 0.039469 | 0.049479 | -0.0032192 | -0.012953 | 9.6519e-07 | 4.0995e-08 | 0.00049116 | 0.1721% | 0.1578% | 3.4866 | 195.4 | -20 | 277.8284 | 300.124 | 195.4 | 38181.1674 | 54287.6723 | 58644.2338 | 56.0434 | 56.5619 | 0.99083
279.5754 | 277.6342 | 299.9596 | 302.0367 | 277.57 | 0.013547 | 0.017077 | UC | 20 | 43.0141 | -110552.9572 | 279.5754 | 277.6342 | 0.0031684 | 0.0031363 | 1.4245e-05 | 1.7927e-05 | 0.068094 | 269.5956 | 0.013738 | 0.015047 | -0.0058656 | -0.0064596 | 4.2563e-07 | -6.2276e-07 | 0.0009441 | 0.2439% | 0.1583% | 2.5702 | 110.553 | -20 | 277.6342 | 299.9596 | 110.553 | 12221.9563 | 30693.2873 | 33161.4191 | 43.0141 | 43.262 | 0.99427
282.9006 | 277.6438 | 291.5501 | 296.4499 | 277.0389 | 0.013574 | 0.016943 | UC | 20 | 59.9766 | -299658.5827 | 282.9006 | 277.6438 | 0.0029435 | 0.0030139 | 1.4268e-05 | 1.7799e-05 | 0.094462 | 423.6553 | 0.0072379 | 0.0079461 | -0.0017965 | -0.0047311 | 1.1732e-06 | 8.8803e-07 | -0.00069565 | 0.1414% | 0.1575% | 4.9963 | 299.6586 | -20 | 277.6438 | 291.5501 | 299.6586 | 89795.2662 | 83198.3578 | 87365.4964 | 59.9766 | 59.2803 | 1.0117
279.8114 | 277.8497 | 291.4498 | 293.4643 | 277.5944 | 0.013531 | 0.017073 | UC | 20 | 35.1645 | -111572.7044 | 279.8114 | 277.8497 | 0.0061149 | 0.0071365 | 1.4229e-05 | 1.794e-05 | 0.061295 | 299.049 | -0.01208 | -0.010128 | -0.031004 | -0.039433 | 2.1788e-06 | 6.3482e-07 | -0.00089823 | 0.268% | 0.1743% | 3.1729 | 111.5727 | -20 | 277.8497 | 291.4498 | 111.5727 | 12448.4684 | 31000.4418 | 32517.8443 | 35.1645 | 35.6183 | 0.98726
289.3771 | 283.552 | 303.3591 | 308.8915 | 282.5944 | 0.01362 | 0.016793 | UC | 30 | 85.5597 | -332135.0311 | 289.3771 | 283.552 | 0.0029264 | 0.002938 | 1.4333e-05 | 1.7634e-05 | 0.13459 | 456.0677 | 0.0017609 | 0.0017508 | 0.00031215 | 0.001703 | -1.3305e-06 | -1.975e-06 | -0.00027234 | 0.1373% | 0.1573% | 3.8819 | 332.135 | -30 | 283.552 | 303.3591 | 332.135 | 110313.6789 | 94177.5369 | 100756.183 | 85.5597 | 85.1577 | 1.0047
284.9557 | 283.3742 | 297.6389 | 299.2231 | 283.15 | 0.013587 | 0.016809 | UC | 30 | 35.5711 | -90067.999 | 284.9557 | 283.3742 | 0.0029499 | 0.0029525 | 1.4284e-05 | 1.7651e-05 | 0.05601 | 258.519 | -0.011306 | -0.010738 | 0.001925 | -8.8821e-05 | -1.0864e-06 | -2.1875e-06 | 0.00085109 | 0.287% | 0.1575% | 2.5321 | 90.068 | -30 | 283.3742 | 297.6389 | 90.068 | 8112.2444 | 25522.9505 | 26807.7447 | 35.5711 | 36.0749 | 0.98603
282.5399 | 280.5899 | 302.9217 | 304.9293 | 280.3722 | 0.013568 | 0.017006 | UC | 30 | 44.6968 | -111044.4834 | 282.5399 | 280.5899 | 0.002934 | 0.0029285 | 1.4263e-05 | 1.7879e-05 | 0.070287 | 269.2501 | -0.014614 | -0.015231 | -0.0024048 | -0.0019079 | -1.3824e-06 | 1.6639e-07 | 0.00050741 | 0.2425% | 0.1573% | 2.4844 | 111.0445 | -30 | 280.5899 | 302.9217 | 111.0445 | 12330.8773 | 31157.9567 | 33637.7875 | 44.6968 | 44.7161 | 0.99957
281.2294 | 277.7677 | 300.3964 | 303.8275 | 277.5944 | 0.013566 | 0.016982 | UC | 30 | 57.1186 | -197314.282 | 281.2294 | 277.7677 | 0.0030131 | 0.0030475 | 1.4265e-05 | 1.7851e-05 | 0.089879 | 331.0645 | 0.00062483 | -0.00041249 | 0.0044354 | 0.0026443 | -9.9413e-07 | 4.1206e-06 | 0.0009441 | 0.1678% | 0.1574% | 3.4545 | 197.3143 | -30 | 277.7677 | 300.3964 | 197.3143 | 38932.9259 | 54807.5352 | 59272.4996 | 57.1186 | 57.2783 | 0.99721
281.1606 | 277.4255 | 294.981 | 298.5871 | 277.0389 | 0.013574 | 0.016986 | UC | 30 | 51.3509 | -213044.2521 | 281.1606 | 277.4255 | 0.0029555 | 0.0029874 | 1.4274e-05 | 1.7837e-05 | 0.080757 | 343.5984 | -0.0030015 | -0.0026432 | 0.00054096 | -0.0034862 | 4.3768e-07 | 3.6413e-07 | -0.0009957 | 0.1613% | 0.1573% | 4.1488 | 213.0443 | -30 | 277.4255 | 294.981 | 213.0443 | 45387.8534 | 59103.8992 | 62844.0094 | 51.3509 | 52.3796 | 0.98036
279.7222 | 277.8673 | 295.0071 | 296.939 | 277.5944 | 0.013546 | 0.01704 | UC | 30 | 37.4424 | -105614.1448 | 279.7222 | 277.8673 | 0.0029514 | 0.0029576 | 1.4242e-05 | 1.7899e-05 | 0.058887 | 266.3324 | 0.021956 | 0.019415 | 0.0029877 | 0.00094707 | -8.3377e-07 | 1.1653e-06 | -0.00097754 | 0.2522% | 0.1573% | 2.8207 | 105.6141 | -30 | 277.8673 | 295.0071 | 105.6141 | 11154.3476 | 29346.7149 | 31156.9271 | 37.4424 | 38.1235 | 0.98213
281.5671 | 277.5616 | 292.1773 | 296.0103 | 277.5944 | 0.013574 | 0.016919 | UC | 30 | 49.7695 | -228429.67 | 281.5671 | 277.5616 | 0.0029405 | 0.0029755 | 1.4275e-05 | 1.7756e-05 | 0.078308 | 357.6166 | 0.011067 | 0.011279 | 0.0015735 | -0.001513 | 1.8924e-06 | -6.2216e-07 | -0.00017391 | 0.1566% | 0.1573% | 4.5898 | 228.4297 | -30 | 277.5616 | 292.1773 | 228.4297 | 52180.1141 | 63403.3046 | 66741.9618 | 49.7695 | 50.3306 | 0.98885
279.6179 | 277.6065 | 292.0755 | 294.1519 | 277.5944 | 0.013542 | 0.016966 | UC | 30 | 36.0541 | -114513.3607 | 279.6179 | 277.6065 | 0.0029536 | 0.0029849 | 1.4253e-05 | 1.7827e-05 | 0.056707 | 271.4291 | 0.010701 | 0.011783 | -0.00058873 | -0.0021235 | 1.266e-06 | 8.1206e-07 | 0.00026374 | 0.237% | 0.1573% | 3.1762 | 114.5134 | -30 | 277.6065 | 292.0755 | 114.5134 | 13113.3098 | 31789.65 | 33446.5492 | 36.0541 | 36.5971 | 0.98516
287.0883 | 283.4784 | 302.8436 | 306.254 | 283.15 | 0.013587 | 0.016931 | UC | 40 | 57.4503 | -205464.7408 | 287.0883 | 283.4784 | 0.0032676 | 0.0036133 | 1.4285e-05 | 1.7782e-05 | 0.098744 | 344.7977 | 0.041556 | 0.028439 | 0.01471 | 0.021876 | -9.5121e-07 | -2.2224e-06 | -6.5637e-05 | 0.1678% | 0.1719% | 3.5764 | 205.4647 | -40 | 283.4784 | 302.8436 | 205.4647 | 42215.7597 | 58244.8136 | 62223.6797 | 57.4503 | 59.2894 | 0.96898
289.4085 | 283.125 | 297.596 | 303.524 | 282.5944 | 0.013588 | 0.016682 | UC | 40 | 75.6907 | -357440.4936 | 289.4085 | 283.125 | 0.0029737 | 0.0029712 | 1.4296e-05 | 1.7552e-05 | 0.1191 | 481.3988 | -0.014014 | -0.014458 | -0.0036545 | -0.0036742 | -9.2842e-07 | -1.3691e-06 | -0.00088772 | 0.1347% | 0.1573% | 4.7224 | 357.4405 | -40 | 283.125 | 297.596 | 357.4405 | 127763.7065 | 101200.3288 | 106372.8725 | 75.6907 | 78.35 | 0.96606
284.8435 | 283.3159 | 297.3253 | 298.8894 | 283.15 | 0.013563 | 0.01682 | UC | 40 | 35.1136 | -86848.7673 | 284.8435 | 283.3159 | 0.0042609 | 0.0046885 | 1.4279e-05 | 1.7676e-05 | 0.055313 | 263.6288 | -0.016939 | -0.021163 | 0.021374 | 0.023327 | 1.6621e-06 | -1.644e-06 | -0.00085905 | 0.3035% | 0.1575% | 2.4734 | 86.8488 | -40 | 283.3159 | 297.3253 | 86.8488 | 7542.7084 | 24605.6396 | 25822.3336 | 35.1136 | 35.4571 | 0.99031
288.0078 | 283.0616 | 294.2924 | 298.8733 | 282.5944 | 0.013584 | 0.016771 | UC | 40 | 56.5103 | -281403.4151 | 288.0078 | 283.0616 | 0.0029691 | 0.0029765 | 1.4286e-05 | 1.7617e-05 | 0.088907 | 405.7547 | -0.0037665 | -0.0051898 | -0.0036832 | -0.0042661 | 1.0219e-06 | -2.0299e-06 | -0.00097946 | 0.1442% | 0.1573% | 4.9797 | 281.4034 | -40 | 283.0616 | 294.2924 | 281.4034 | 79187.882 | 79654.5008 | 82814.8776 | 56.5103 | 58.6543 | 0.96345
286.4908 | 283.0524 | 291.7523 | 294.9455 | 283.15 | 0.013589 | 0.01688 | UC | 40 | 41.9916 | -195786.3919 | 286.4908 | 283.0524 | 0.0030838 | 0.0033904 | 1.4286e-05 | 1.7726e-05 | 0.066034 | 329.4685 | -0.00099591 | -0.00058077 | -0.0055009 | -0.012651 | -2.11e-06 | 4.9918e-07 | 3.5356e-05 | 0.1683% | 0.1573% | 4.6625 | 195.7864 | -40 | 283.0524 | 291.7523 | 195.7864 | 38332.3113 | 55417.8044 | 57121.1221 | 41.9916 | 42.8824 | 0.97923
285.0855 | 283.0706 | 290.423 | 292.3132 | 283.15 | 0.013566 | 0.017025 | UC | 40 | 33.0531 | -114583.6926 | 285.0855 | 283.0706 | 0.0031855 | 0.0036967 | 1.4271e-05 | 1.7876e-05 | 0.052189 | 275.9481 | -0.005391 | -0.003069 | -0.0073462 | -0.014459 | -2.145e-06 | 5.9081e-08 | 3.7267e-05 | 0.2408% | 0.1579% | 3.4667 | 114.5837 | -40 | 283.0706 | 290.423 | 114.5837 | 13129.4226 | 32435.2716 | 33277.7346 | 33.0531 | 32.6919 | 1.011
286.0982 | 280.7049 | 302.9389 | 308.1098 | 279.8167 | 0.013584 | 0.016865 | UC | 40 | 82.2244 | -307144.1862 | 286.0982 | 280.7049 | 0.0029649 | 0.0029309 | 1.4281e-05 | 1.7733e-05 | 0.12933 | 430.7538 | -0.013643 | -0.01209 | -0.0049955 | -0.00067314 | 5.2872e-07 | 1.6862e-06 | 0.00090301 | 0.1402% | 0.1573% | 3.7354 | 307.1442 | -40 | 280.7049 | 302.9389 | 307.1442 | 94337.5511 | 86216.8732 | 93045.9372 | 82.2244 | 80.6021 | 1.0201
282.0287 | 280.4216 | 297.1529 | 298.8325 | 280.3661 | 0.01356 | 0.016975 | UC | 40 | 36.4 | -91484.7828 | 282.0287 | 280.4216 | 0.0029412 | 0.0029274 | 1.4262e-05 | 1.7843e-05 | 0.057238 | 258.4278 | -0.0031067 | -0.0025402 | 0.0026974 | 0.0010978 | -1.0984e-06 | -1.1617e-06 | 0.00095939 | 0.2825% | 0.1572% | 2.5133 | 91.4848 | -40 | 280.4216 | 297.1529 | 91.4848 | 8369.4655 | 25654.3047 | 27184.9713 | 36.4 | 37.1185 | 0.98064
282.2777 | 280.3715 | 291.6616 | 293.5318 | 280.3722 | 0.013558 | 0.017037 | UC | 40 | 34.0742 | -108485.7629 | 282.2777 | 280.3715 | 0.0030508 | 0.003087 | 1.4256e-05 | 1.7898e-05 | 0.053595 | 267.8507 | -0.019382 | -0.020384 | 0.0012698 | 0.00047778 | 1.2497e-06 | -2.23e-06 | 0.00088581 | 0.2469% | 0.1573% | 3.1838 | 108.4858 | -40 | 280.3715 | 291.6616 | 108.4858 | 11769.1607 | 30416.3149 | 31641.1311 | 34.0742 | 34.4014 | 0.99049
279.862 | 277.9173 | 299.7605 | 301.8288 | 277.5944 | 0.01354 | 0.017054 | UC | 40 | 42.5715 | -110673.6512 | 279.862 | 277.9173 | 0.0029832 | 0.0029843 | 1.4244e-05 | 1.7923e-05 | 0.06695 | 268.4886 | -0.0029453 | -0.0036651 | 0.0033254 | 0.0014854 | -1.2823e-06 | 1.3667e-06 | 0.00048925 | 0.2426% | 0.1573% | 2.5997 | 110.6737 | -40 | 277.9173 | 299.7605 | 110.6737 | 12248.6571 | 30758.1198 | 33175.5891 | 42.5715 | 42.977 | 0.99056
283.1305 | 278.0023 | 291.4993 | 296.3242 | 277.0389 | 0.013567 | 0.016932 | UC | 40 | 59.5341 | -292130.0771 | 283.1305 | 278.0023 | 0.0029305 | 0.0029345 | 1.4252e-05 | 1.7783e-05 | 0.093659 | 415.8724 | 0.0042101 | 0.0030924 | 0.00050355 | 0.0013375 | -7.061e-07 | -9.0428e-07 | -0.00088883 | 0.1424% | 0.1573% | 4.9069 | 292.1301 | -40 | 278.0023 | 291.4993 | 292.1301 | 85339.9819 | 81212.8391 | 85155.7213 | 59.5341 | 57.8852 | 1.0285
281.6242 | 277.8814 | 291.5716 | 295.1457 | 277.5944 | 0.013546 | 0.016909 | UC | 40 | 46.9936 | -212990.6466 | 281.6242 | 277.8814 | 0.0029176 | 0.0029337 | 1.4172e-05 | 1.7666e-05 | 0.073495 | 341.4087 | 0.0011131 | 0.0003797 | -0.00039944 | -0.0019629 | -1.5247e-06 | -1.1939e-06 | -0.00086317 | 0.1603% | 0.1564% | 4.5323 | 212.9906 | -40 | 277.8814 | 291.5716 | 212.9906 | 45365.0155 | 59186.1393 | 62102.0275 | 46.9936 | 47.2703 | 0.99415
279.687 | 277.7567 | 291.2959 | 293.2949 | 277.5944 | 0.013525 | 0.01693 | UC | 40 | 34.8418 | -109747.6319 | 279.687 | 277.7567 | 0.0029573 | 0.0029532 | 1.414e-05 | 1.7694e-05 | 0.054525 | 266.833 | -0.019614 | -0.018022 | 0.00035859 | -0.0017806 | -3.203e-07 | -1.9218e-06 | -0.00025569 | 0.2431% | 0.1565% | 3.1499 | 109.7476 | -40 | 277.7567 | 291.2959 | 109.7476 | 12044.5427 | 30483.1404 | 31969.0345 | 34.8418 | 35.3378 | 0.98597
286.7684 | 283.2836 | 302.6867 | 306.027 | 283.15 | 0.013584 | 0.016911 | UC | 40 | 56.4979 | -198324.6977 | 286.7684 | 283.2836 | 0.0030884 | 0.0034673 | 1.4291e-05 | 1.7765e-05 | 0.089347 | 332.5462 | 0.01999 | 0.01975 | -0.00075065 | -0.0061719 | -1.9732e-06 | 9.9654e-07 | 0.00026756 | 0.1677% | 0.1581% | 3.5103 | 198.3247 | -40 | 283.2836 | 302.6867 | 198.3247 | 39332.6857 | 56182.1299 | 60030.2465 | 56.4979 | 57.89 | 0.97595
289.257 | 283.0788 | 297.3394 | 303.1819 | 282.5944 | 0.01361 | 0.016668 | UC | 40 | 73.6295 | -352030.8682 | 289.257 | 283.0788 | 0.0030033 | 0.0030827 | 1.4313e-05 | 1.7522e-05 | 0.11588 | 477.2945 | -0.016168 | -0.019154 | -0.0053581 | -0.0012491 | 1.761e-06 | 2.0069e-06 | 0.00063927 | 0.1356% | 0.1574% | 4.7811 | 352.0309 | -40 | 283.0788 | 297.3394 | 352.0309 | 123925.7322 | 99652.4812 | 104672.6606 | 73.6295 | 76.7919 | 0.95882
284.806 | 283.4539 | 296.579 | 298.062 | 283.15 | 0.013574 | 0.016901 | UC | 40 | 33.2834 | -76933.0569 | 284.806 | 283.4539 | 0.0084512 | 0.010904 | 1.4282e-05 | 1.7777e-05 | 0.14342 | 543.245 | 0.0015326 | 0.0054478 | -0.0062043 | -0.013301 | -1.3474e-06 | 1.6416e-06 | 0.0001376 | 0.7061% | 0.4309% | 2.3115 | 76.9331 | -40 | 283.4539 | 296.579 | 76.9331 | 5918.6952 | 21806.9756 | 22816.729 | 33.2834 | 33.6618 | 0.98876
288.0303 | 282.9596 | 294.3938 | 299.1232 | 282.5944 | 0.013599 | 0.016738 | UC | 40 | 57.9058 | -288810.4361 | 288.0303 | 282.9596 | 0.0029647 | 0.0029623 | 1.4299e-05 | 1.7599e-05 | 0.091143 | 414.4741 | -0.012848 | -0.016957 | -0.0049689 | -0.0041089 | 8.2472e-07 | 1.2057e-08 | 0.00013569 | 0.1435% | 0.1574% | 4.9876 | 288.8104 | -40 | 282.9596 | 294.3938 | 288.8104 | 83411.468 | 81721.6811 | 85024.0116 | 57.9058 | 60.0501 | 0.96429
286.5016 | 283.0361 | 291.7007 | 294.9016 | 283.15 | 0.013584 | 0.016864 | UC | 40 | 42.0475 | -197260.8494 | 286.5016 | 283.0361 | 0.0029507 | 0.0032335 | 1.4289e-05 | 1.7729e-05 | 0.066589 | 334.9751 | -0.0037623 | -0.0043717 | -0.0025482 | -0.0078818 | 1.0785e-06 | -1.4825e-06 | -0.00075776 | 0.1698% | 0.1584% | 4.6914 | 197.2608 | -40 | 283.0361 | 291.7007 | 197.2608 | 38911.8427 | 55831.9497 | 57541.1343 | 42.0475 | 42.9988 | 0.97788
285.0871 | 283.2582 | 290.073 | 291.8291 | 283.15 | 0.013582 | 0.017015 | UC | 40 | 31.8916 | -104124.7492 | 285.0871 | 283.2582 | 0.0035537 | 0.0046587 | 1.4296e-05 | 1.7875e-05 | 0.059229 | 322.7355 | -0.0097027 | -0.012368 | 0.00090301 | -0.00066146 | 2.154e-06 | 1.5554e-07 | 5.3512e-05 | 0.31% | 0.1857% | 3.265 | 104.1247 | -40 | 283.2582 | 290.073 | 104.1247 | 10841.9634 | 29494.1934 | 30203.7737 | 31.8916 | 31.3464 | 1.0174
283.9963 | 280.6111 | 302.7775 | 306.0954 | 280.3722 | 0.013577 | 0.016929 | UC | 40 | 57.9724 | -192822.8822 | 283.9963 | 280.6111 | 0.0029365 | 0.0029903 | 1.4275e-05 | 1.78e-05 | 0.091186 | 326.8138 | -0.0061682 | -0.0077735 | 0.00059033 | -3.5568e-05 | 1.5554e-06 | 1.7978e-06 | 0.00019111 | 0.1695% | 0.1573% | 3.3261 | 192.8229 | -40 | 280.6111 | 302.7775 | 192.8229 | 37180.6639 | 54108.2314 | 58382.4367 | 57.9724 | 58.3177 | 0.99408
286.493 | 280.4507 | 297.1641 | 302.8997 | 279.8167 | 0.013603 | 0.016829 | UC | 40 | 75.8831 | -344570.059 | 286.493 | 280.4507 | 0.002968 | 0.0030058 | 1.4297e-05 | 1.77e-05 | 0.12213 | 468.5656 | -0.00026544 | -0.0038053 | 0.0027462 | 0.0070165 | -7.4635e-07 | -1.2618e-06 | -0.00058672 | 0.136% | 0.161% | 4.5408 | 344.5701 | -40 | 280.4507 | 297.1641 | 344.5701 | 118728.5255 | 96634.9044 | 102393.8523 | 75.8831 | 76.4933 | 0.99202
283.2962 | 279.9882 | 297.0792 | 300.3437 | 279.8533 | 0.013574 | 0.016932 | UC | 40 | 49.0105 | -188443.9568 | 283.2962 | 279.9882 | 0.0045797 | 0.0063652 | 1.4273e-05 | 1.7794e-05 | 0.081773 | 353.9356 | -0.014234 | -0.00084992 | -0.013256 | -0.029527 | 5.0762e-07 | -1.0671e-07 | -0.00070712 | 0.1878% | 0.1668% | 3.845 | 188.444 | -40 | 279.9882 | 297.0792 | 188.444 | 35511.1249 | 52762.0875 | 55982.7765 | 49.0105 | 50.4095 | 0.97225
282.0087 | 280.3651 | 297.0781 | 298.8205 | 280.3722 | 0.013558 | 0.016962 | UC | 40 | 36.6484 | -93549.1739 | 282.0087 | 280.3651 | 0.0034181 | 0.0038541 | 1.425e-05 | 1.783e-05 | 0.058585 | 263.2592 | -0.0097696 | -0.0065228 | -0.0062202 | -0.010205 | 2.7491e-07 | -2.6189e-06 | 8.5045e-05 | 0.2814% | 0.1599% | 2.5526 | 93.5492 | -40 | 280.3651 | 297.0781 | 93.5492 | 8751.4479 | 26227.9273 | 27791.4093 | 36.6484 | 37.3379 | 0.98153
286.1744 | 280.2874 | 294.3926 | 299.9419 | 279.8167 | 0.013587 | 0.016822 | UC | 40 | 68.7009 | -335375.9096 | 286.1744 | 280.2874 | 0.0030247 | 0.0031463 | 1.4282e-05 | 1.7679e-05 | 0.10821 | 459.5377 | -0.0078818 | -0.0086691 | -0.0048798 | -0.0061491 | -7.4876e-07 | 2.0763e-06 | 0.00087721 | 0.137% | 0.1575% | 4.8817 | 335.3759 | -40 | 280.2874 | 294.3926 | 335.3759 | 112477.0007 | 94001.6497 | 98732.1903 | 68.7009 | 69.1466 | 0.99355
281.3151 | 277.9432 | 299.7866 | 303.1328 | 277.5944 | 0.013569 | 0.016999 | UC | 40 | 56.3311 | -192229.7127 | 281.3151 | 277.9432 | 0.0029221 | 0.0029325 | 1.4269e-05 | 1.7864e-05 | 0.088882 | 326.0589 | 0.0036651 | 0.0034676 | 0.0015926 | 0.002253 | -3.6896e-07 | 1.6561e-06 | 0.00011467 | 0.1696% | 0.1578% | 3.4125 | 192.2297 | -40 | 277.9432 | 299.7866 | 192.2297 | 36952.2624 | 53428.9343 | 57627.8978 | 56.3311 | 55.5335 | 1.0144
279.5245 | 277.5505 | 299.7649 | 301.8674 | 277.6555 | 0.013534 | 0.017052 | UC | 40 | 43.2324 | -112313.672 | 279.5245 | 277.5505 | 0.0029308 | 0.0029311 | 1.4224e-05 | 1.7921e-05 | 0.067982 | 269.3199 | -0.001969 | -0.0015523 | 0.0020343 | 0.0012762 | -1.2226e-06 | -2.5501e-07 | -0.00082465 | 0.2398% | 0.1572% | 2.5979 | 112.3137 | -40 | 277.5505 | 299.7649 | 112.3137 | 12614.3609 | 31172.7214 | 33667.6962 | 43.2324 | 43.3767 | 0.99667
280.8937 | 277.3933 | 293.8264 | 297.2435 | 277.0389 | 0.013556 | 0.017027 | UC | 40 | 49.4981 | -199407.2776 | 280.8937 | 277.3933 | 0.0030032 | 0.0031587 | 1.425e-05 | 1.7876e-05 | 0.077839 | 332.0327 | -0.0016712 | -0.00069863 | -0.002442 | -0.0084716 | 1.5669e-06 | -6.9089e-07 | -0.00086765 | 0.1665% | 0.1573% | 4.0286 | 199.4073 | -40 | 277.3933 | 293.8264 | 199.4073 | 39763.2624 | 55314.2519 | 58591.1294 | 49.4981 | 48.8756 | 1.0127
279.6319 | 278.0214 | 293.0977 | 294.8396 | 277.5944 | 0.013554 | 0.017079 | UC | 40 | 34.747 | -91770.0216 | 279.6319 | 278.0214 | 0.0081943 | 0.010572 | 1.4247e-05 | 1.794e-05 | 0.15183 | 539.7179 | -0.0015746 | 0.0056734 | -0.019141 | -0.027105 | -1.7718e-06 | -1.6157e-07 | -0.00094028 | 0.5881% | 0.4369% | 2.6411 | 91.77 | -40 | 278.0214 | 293.0977 | 91.77 | 8421.7369 | 25514.0325 | 26897.586 | 34.747 | 34.9239 | 0.99494
282.7151 | 277.7847 | 290.7239 | 295.3523 | 277.0389 | 0.013575 | 0.016943 | UC | 40 | 57.2205 | -281075.4835 | 282.7151 | 277.7847 | 0.0029848 | 0.002988 | 1.4287e-05 | 1.7802e-05 | 0.090021 | 405.6507 | 0.0086808 | 0.0090195 | -0.0041429 | -0.0033593 | 1.6591e-06 | 2.2909e-06 | 0.00057716 | 0.1443% | 0.1573% | 4.9121 | 281.0755 | -40 | 277.7847 | 290.7239 | 281.0755 | 79003.4274 | 78078.4794 | 81715.3696 | 57.2205 | 55.0165 | 1.0401
280.9172 | 277.5601 | 289.7252 | 292.9335 | 277.5944 | 0.013562 | 0.016954 | UC | 40 | 42.44 | -191331.4235 | 280.9172 | 277.5601 | 0.0030458 | 0.0031297 | 1.4257e-05 | 1.7808e-05 | 0.066773 | 325.833 | 0.015484 | 0.013411 | -0.00092424 | -0.0024877 | -1.1762e-06 | -1.4975e-06 | -0.00099188 | 0.1703% | 0.1573% | 4.5083 | 191.3314 | -40 | 277.5601 | 289.7252 | 191.3314 | 36607.7136 | 53105.9756 | 55433.5376 | 42.44 | 42.305 | 1.0032
279.4461 | 277.8225 | 289.2549 | 290.9529 | 277.5944 | 0.01355 | 0.016975 | UC | 40 | 31.4876 | -92482.9389 | 279.4461 | 277.8225 | 0.0037899 | 0.0034074 | 1.4242e-05 | 1.7831e-05 | 0.049561 | 261.294 | -0.0079986 | -0.0073281 | -0.011129 | -0.0079657 | -9.037e-07 | -9.6881e-07 | -0.00037649 | 0.2825% | 0.1574% | 2.9371 | 92.4829 | -40 | 277.8225 | 289.2549 | 92.4829 | 8553.094 | 25693.8438 | 26751.1418 | 31.4876 | 31.9875 | 0.98437

## test_file_OC
TEI_K_mean | TEO_K_mean | TCI_K_mean | TCO_K_mean | TWE_set_K_mean | FWE_m3s_mean | FWC_m3s_mean | fault_type | fault_level | kW_mean | q_evap_mean_inst | TEI_K_mean | TEO_K_mean | TCI_K_mean_uncer | TCO_K_mean_uncer | FWE_m3s_mean_uncer | FWC_m3s_mean_uncer | kW_mean_uncer | q_uncer_evap_mean_inst | TEI_K_abs_slope | TEO_K_abs_slope | TCI_K_abs_slope | TCO_K_abs_slope | FWE_m3s_rel_slope | FWC_m3s_rel_slope | kW_rel_slope | rel_uncer_q | rel_uncer_kW | COP | Cooling capacity [kW] | Fault level | TEO_K_mean | TCI_K_mean | Cooling capacity [kW] | Q^2 | TEO*Q | TCI*Q | kW_mean | kW_NF | kW/kW_NF
286.8916 | 283.4214 | 297.6888 | 301.0009 | 283.15 | 0.013596 | 0.016886 | OC | 10 | 50.8607 | -197667.2088 | 286.8916 | 283.4214 | 0.0034499 | 0.0049931 | 1.4304e-05 | 1.7743e-05 | 0.084335 | 354.5762 | 0.0079116 | 0.012575 | 0.0040983 | -0.0043972 | 2.3259e-06 | 6.2578e-07 | -0.00091161 | 0.1794% | 0.1658% | 3.8864 | 197.6672 | 10 | 283.4214 | 297.6888 | 197.6672 | 39072.3254 | 56023.1227 | 58843.3076 | 50.8607 | 50.9533 | 0.99818
284.6546 | 283.0837 | 297.6448 | 299.2488 | 283.15 | 0.013599 | 0.016866 | OC | 10 | 36.1904 | -89564.3403 | 284.6546 | 283.0837 | 0.0029582 | 0.0029453 | 1.4307e-05 | 1.7721e-05 | 0.05691 | 257.6423 | -0.001805 | -0.0028455 | 0.0039199 | 0.0025312 | -3.622e-06 | -3.1952e-07 | -0.00078165 | 0.2877% | 0.1573% | 2.4748 | 89.5643 | 10 | 283.0837 | 297.6448 | 89.5643 | 8021.7711 | 25354.2048 | 26658.3611 | 36.1904 | 36.1402 | 1.0014
287.9697 | 282.7974 | 294.8574 | 299.7073 | 282.5944 | 0.013618 | 0.016795 | OC | 10 | 62.3167 | -295030.5551 | 287.9697 | 282.7974 | 0.0030223 | 0.0030941 | 1.4316e-05 | 1.765e-05 | 0.098033 | 419.247 | 0.0096656 | 0.0087694 | 0.00044805 | -0.002391 | -2.7672e-07 | -6.6135e-07 | -0.00066316 | 0.1421% | 0.1573% | 4.7344 | 295.0306 | 10 | 282.7974 | 294.8574 | 295.0306 | 87043.0284 | 83433.8845 | 86991.9566 | 62.3167 | 61.983 | 1.0054
286.6266 | 283.0395 | 292.2103 | 295.5561 | 283.15 | 0.013619 | 0.016923 | OC | 10 | 45.139 | -204687.7739 | 286.6266 | 283.0395 | 0.0029479 | 0.0031119 | 1.4325e-05 | 1.7776e-05 | 0.070995 | 338.0078 | 0.0011573 | 0.0053294 | -0.0006604 | -0.0068461 | -9.887e-08 | 1.1177e-06 | 0.00043574 | 0.1651% | 0.1573% | 4.5346 | 204.6878 | 10 | 283.0395 | 292.2103 | 204.6878 | 41897.0848 | 57934.7251 | 59811.8669 | 45.139 | 44.6071 | 1.0119
283.8472 | 280.4259 | 303.1304 | 306.4787 | 279.8167 | 0.01359 | 0.016975 | OC | 10 | 61.6515 | -195078.2154 | 283.8472 | 280.4259 | 0.0029861 | 0.0030052 | 1.4289e-05 | 1.7831e-05 | 0.097124 | 329.0349 | -0.029197 | -0.030353 | -0.0035563 | -0.0013739 | -1.5807e-06 | 3.059e-06 | -0.00029336 | 0.1687% | 0.1575% | 3.1642 | 195.0782 | 10 | 280.4259 | 303.1304 | 195.0782 | 38055.5101 | 54704.9932 | 59134.1381 | 61.6515 | 59.2815 | 1.04
282.2661 | 280.6237 | 297.4568 | 299.131 | 280.3722 | 0.01358 | 0.017012 | OC | 10 | 37.2785 | -93623.7558 | 282.2661 | 280.6237 | 0.0031292 | 0.0030743 | 1.4286e-05 | 1.787e-05 | 0.058647 | 261.4165 | -0.00019483 | -0.0025604 | 0.0072188 | 0.004446 | 1.31e-06 | -1.7935e-06 | -5.0645e-05 | 0.2792% | 0.1573% | 2.5115 | 93.6238 | 10 | 280.6237 | 297.4568 | 93.6238 | 8765.4076 | 26273.0436 | 27849.0206 | 37.2785 | 37.5441 | 0.99292
279.5814 | 277.7703 | 294.915 | 296.8045 | 277.5944 | 0.013561 | 0.017045 | OC | 10 | 37.739 | -103243.6493 | 279.5814 | 277.7703 | 0.0030634 | 0.0031173 | 1.426e-05 | 1.7909e-05 | 0.059358 | 264.9237 | -0.0083941 | -0.0094389 | 0.0057552 | 0.0066847 | -7.0536e-07 | 2.0287e-06 | -0.00020258 | 0.2566% | 0.1573% | 2.7357 | 103.2436 | 10 | 277.7703 | 294.915 | 103.2436 | 10659.2511 | 28678.0225 | 30448.1027 | 37.739 | 37.8081 | 0.99817
279.5077 | 277.5353 | 291.4566 | 293.4967 | 277.5944 | 0.01357 | 0.016988 | OC | 10 | 36.0199 | -112517.272 | 279.5077 | 277.5353 | 0.0069757 | 0.0057502 | 1.4269e-05 | 1.7842e-05 | 0.056963 | 280.0333 | 0.010205 | 0.0059542 | -0.032011 | -0.024954 | -1.2636e-06 | -9.9534e-07 | 0.00075012 | 0.2489% | 0.1581% | 3.1238 | 112.5173 | 10 | 277.5353 | 291.4566 | 112.5173 | 12660.1365 | 31227.5202 | 32793.9008 | 36.0199 | 35.8568 | 1.0045
285.2272 | 283.3627 | 302.8593 | 304.7632 | 283.15 | 0.013576 | 0.016973 | OC | 20 | 43.0881 | -106093.6893 | 285.2272 | 283.3627 | 0.0029748 | 0.0029867 | 1.4362e-05 | 1.793e-05 | 0.068417 | 269.4304 | -0.022218 | -0.026069 | -0.00062674 | -0.00014784 | -1.4691e-07 | 1.1835e-06 | 0.00027271 | 0.254% | 0.1588% | 2.4622 | 106.0937 | 20 | 283.3627 | 302.8593 | 106.0937 | 11255.8709 | 30062.996 | 32131.4562 | 43.0881 | 42.6784 | 1.0096
286.9051 | 283.3443 | 297.5481 | 300.9521 | 283.15 | 0.013591 | 0.016753 | OC | 20 | 51.4985 | -202746.5487 | 286.9051 | 283.3443 | 0.0029699 | 0.0029732 | 1.4298e-05 | 1.7596e-05 | 0.080996 | 335.0016 | -0.0085237 | -0.0084833 | 0.0011 | -0.00023995 | -7.6625e-07 | 1.5705e-06 | 0.00053416 | 0.1652% | 0.1573% | 3.9369 | 202.7465 | 20 | 283.3443 | 297.5481 | 202.7465 | 41106.163 | 57447.0835 | 60326.8519 | 51.4985 | 51.5702 | 0.99861
286.6576 | 283.0949 | 292.1981 | 295.5438 | 283.15 | 0.013593 | 0.016858 | OC | 20 | 44.9203 | -202917.9708 | 286.6576 | 283.0949 | 0.003154 | 0.0040342 | 1.4302e-05 | 1.7707e-05 | 0.07111 | 342.7452 | -0.002073 | 0.0017391 | -0.0061512 | -0.016621 | -2.0877e-06 | 2.8305e-06 | 0.00098041 | 0.1689% | 0.1583% | 4.5173 | 202.918 | 20 | 283.0949 | 292.1981 | 202.918 | 41175.7029 | 57445.0493 | 59292.247 | 44.9203 | 44.3424 | 1.013
285.1634 | 282.9825 | 291.0973 | 293.1554 | 283.0401 | 0.013597 | 0.017028 | OC | 20 | 35.2411 | -124305.7378 | 285.1634 | 282.9825 | 0.0032478 | 0.0035428 | 1.4297e-05 | 1.7944e-05 | 0.05618 | 279.6703 | -0.0033381 | 0.0019233 | -0.012789 | -0.017274 | 2.0606e-06 | 4.8899e-06 | -0.00060774 | 0.225% | 0.1594% | 3.5273 | 124.3057 | 20 | 282.9825 | 291.0973 | 124.3057 | 15451.9165 | 35176.3458 | 36185.0588 | 35.2411 | 34.3036 | 1.0273
282.6134 | 280.691 | 302.8193 | 304.8194 | 280.3722 | 0.013577 | 0.017 | OC | 20 | 45.0149 | -109535.7623 | 282.6134 | 280.691 | 0.0046421 | 0.0061542 | 1.4285e-05 | 1.7862e-05 | 0.07747 | 290.2711 | 0.01226 | 0.015965 | -0.010587 | -0.014173 | 2.1625e-06 | 2.2125e-07 | -4.0134e-05 | 0.265% | 0.1721% | 2.4333 | 109.5358 | 20 | 280.691 | 302.8193 | 109.5358 | 11998.0832 | 30745.7055 | 33169.542 | 45.0149 | 44.3417 | 1.0152
283.4671 | 279.7971 | 291.912 | 295.3345 | 279.8167 | 0.013587 | 0.017226 | OC | 20 | 46.7643 | -209267.2428 | 283.4671 | 279.7971 | 0.004085 | 0.0059488 | 1.4282e-05 | 1.8094e-05 | 0.07365 | 351.8269 | -0.0016064 | 0.0045814 | -0.015218 | -0.031801 | -9.3143e-07 | -9.9172e-07 | 0.00051027 | 0.1681% | 0.1575% | 4.4749 | 209.2672 | 20 | 279.7971 | 291.912 | 209.2672 | 43792.7789 | 58552.3741 | 61087.6122 | 46.7643 | 46.3452 | 1.009
282.2289 | 280.3655 | 291.8173 | 293.6766 | 280.3722 | 0.013569 | 0.016977 | OC | 20 | 34.5686 | -106136.1342 | 282.2289 | 280.3655 | 0.0030529 | 0.0031761 | 1.4265e-05 | 1.7832e-05 | 0.054832 | 268.8015 | 0.0018681 | 0.0036641 | -0.00032595 | -0.0003026 | 1.2021e-06 | 9.3987e-07 | 0.00023794 | 0.2533% | 0.1586% | 3.0703 | 106.1361 | 20 | 280.3655 | 291.8173 | 106.1361 | 11264.879 | 29756.911 | 30972.3642 | 34.5686 | 34.3072 | 1.0076
281.524 | 278.1705 | 300.1274 | 303.4502 | 277.6555 | 0.013559 | 0.016983 | OC | 20 | 57.4398 | -191010.0537 | 281.524 | 278.1705 | 0.002931 | 0.0029404 | 1.4271e-05 | 1.7841e-05 | 0.090375 | 325.182 | -0.012466 | -0.012747 | -3.3976e-05 | 0.00072411 | -4.4353e-06 | -3.3158e-08 | -0.00050741 | 0.1702% | 0.1573% | 3.3254 | 191.0101 | 20 | 278.1705 | 300.1274 | 191.0101 | 36484.8406 | 53133.3529 | 57327.353 | 57.4398 | 55.6735 | 1.0317
280.7051 | 277.1949 | 294.0845 | 297.5159 | 277.0389 | 0.013547 | 0.016996 | OC | 20 | 50.4241 | -199859.2206 | 280.7051 | 277.1949 | 0.0029628 | 0.0029849 | 1.4238e-05 | 1.785e-05 | 0.079321 | 332.5297 | 0.0081558 | 0.0099379 | -0.00047354 | -0.0034337 | -7.8674e-07 | 1.7061e-06 | -0.00063258 | 0.1664% | 0.1573% | 3.9636 | 199.8592 | 20 | 277.1949 | 294.0845 | 199.8592 | 39943.708 | 55399.951 | 58775.4976 | 50.4241 | 49.3843 | 1.0211
279.4198 | 277.6593 | 294.0994 | 295.9679 | 277.5944 | 0.013543 | 0.017047 | OC | 20 | 36.6698 | -100235.1316 | 279.4198 | 277.6593 | 0.0030258 | 0.0030399 | 1.4243e-05 | 1.7916e-05 | 0.057736 | 262.9852 | 0.0058141 | 0.0057069 | 8.9186e-05 | -0.0029458 | 1.2311e-06 | 1.6428e-06 | 0.00096894 | 0.2624% | 0.1574% | 2.7335 | 100.2351 | 20 | 277.6593 | 294.0994 | 100.2351 | 10047.0816 | 27831.2206 | 29479.091 | 36.6698 | 36.8167 | 0.99601
281.56 | 277.9241 | 291.3726 | 294.8777 | 277.5944 | 0.01357 | 0.01691 | OC | 20 | 47.4501 | -207277.7753 | 281.56 | 277.9241 | 0.00308 | 0.0031615 | 1.4262e-05 | 1.7785e-05 | 0.074729 | 339.9183 | -0.0069204 | -0.0097797 | -0.0010171 | -0.00031162 | 1.3577e-06 | 1.0014e-06 | -0.00055327 | 0.164% | 0.1575% | 4.3683 | 207.2778 | 20 | 277.9241 | 291.3726 | 207.2778 | 42964.0761 | 57607.4922 | 60395.0746 | 47.4501 | 46.2511 | 1.0259
279.7784 | 277.8261 | 291.7462 | 293.7739 | 277.5944 | 0.013537 | 0.016943 | OC | 20 | 36.2916 | -111088.3421 | 279.7784 | 277.8261 | 0.0030525 | 0.0030947 | 1.4236e-05 | 1.7792e-05 | 0.057117 | 270.3166 | -0.026472 | -0.02737 | 0.0039996 | 0.0022297 | -1.6886e-06 | -1.7302e-07 | -0.00058194 | 0.2433% | 0.1574% | 3.061 | 111.0883 | 20 | 277.8261 | 291.7462 | 111.0883 | 12340.6198 | 30863.2441 | 32409.6033 | 36.2916 | 35.8472 | 1.0124
287.0063 | 283.5676 | 302.7763 | 306.3588 | 282.5944 | 0.013594 | 0.016993 | OC | 30 | 61.9598 | -195822.6862 | 287.0063 | 283.5676 | 0.0029377 | 0.0030431 | 1.4305e-05 | 1.7853e-05 | 0.097481 | 329.3083 | 0.0046067 | 0.0044801 | 0.0024163 | 0.0021858 | -4.1547e-07 | -1.2552e-06 | -0.00044083 | 0.1682% | 0.1573% | 3.1605 | 195.8227 | 30 | 283.5676 | 302.7763 | 195.8227 | 38346.5244 | 55528.9657 | 59290.4708 | 61.9598 | 57.4295 | 1.0789
286.8141 | 283.4049 | 297.3981 | 300.8627 | 283.15 | 0.013592 | 0.016821 | OC | 30 | 52.0383 | -194122.6591 | 286.8141 | 283.4049 | 0.0029815 | 0.0030347 | 1.439e-05 | 1.7782e-05 | 0.082286 | 329.7383 | -0.011536 | -0.010582 | -7.6508e-05 | 0.0017278 | -3.2855e-07 | -8.0064e-06 | 0.00070824 | 0.1699% | 0.1581% | 3.7304 | 194.1227 | 30 | 283.4049 | 297.3981 | 194.1227 | 37683.6068 | 55015.3202 | 57731.7193 | 52.0383 | 50.038 | 1.04
284.654 | 283.106 | 297.3562 | 299.0484 | 283.15 | 0.013585 | 0.016846 | OC | 30 | 36.3382 | -88157.3459 | 284.654 | 283.106 | 0.0032701 | 0.0031329 | 1.4293e-05 | 1.769e-05 | 0.057156 | 258.6258 | -0.017804 | -0.020605 | 0.012463 | 0.0085125 | -2.8648e-06 | 1.4776e-06 | -0.00032776 | 0.2934% | 0.1573% | 2.426 | 88.1573 | 30 | 283.106 | 297.3562 | 88.1573 | 7771.7176 | 24957.8774 | 26214.1358 | 36.3382 | 35.73 | 1.017
286.5993 | 283.1772 | 291.8946 | 295.2602 | 283.15 | 0.013587 | 0.016904 | OC | 30 | 44.6202 | -194822.5313 | 286.5993 | 283.1772 | 0.0033668 | 0.0045046 | 1.4293e-05 | 1.7767e-05 | 0.070895 | 340.6042 | 0.0056968 | 0.012091 | -0.0038483 | -0.017778 | -1.5234e-06 | 3.1319e-06 | -3.9178e-05 | 0.1748% | 0.1589% | 4.3662 | 194.8225 | 30 | 283.1772 | 291.8946 | 194.8225 | 37955.8187 | 55169.3044 | 56867.6502 | 44.6202 | 42.8966 | 1.0402
285.1114 | 280.5672 | 300.5208 | 305.04 | 279.8167 | 0.013582 | 0.016984 | OC | 30 | 70.3644 | -258854.2682 | 285.1114 | 280.5672 | 0.0029645 | 0.0031871 | 1.4286e-05 | 1.7846e-05 | 0.1107 | 384.8749 | -0.024183 | -0.026262 | -0.0024139 | 0.0070935 | 8.5065e-07 | -1.3082e-06 | -0.0008151 | 0.1487% | 0.1573% | 3.6788 | 258.8543 | 30 | 280.5672 | 300.5208 | 258.8543 | 67005.5322 | 72626.0056 | 77791.0806 | 70.3644 | 66.8955 | 1.0519
282.2974 | 280.3546 | 292.4126 | 294.4348 | 280.3722 | 0.013562 | 0.016956 | OC | 30 | 35.7657 | -110593.6115 | 282.2974 | 280.3546 | 0.0034132 | 0.0038314 | 1.4264e-05 | 1.7826e-05 | 0.058409 | 278.1971 | -0.011515 | -0.013454 | 0.0013022 | 0.00026862 | -3.1325e-06 | 1.1039e-06 | -0.00014238 | 0.2515% | 0.1633% | 3.0922 | 110.5936 | 30 | 280.3546 | 292.4126 | 110.5936 | 12230.9469 | 31005.4321 | 32338.9696 | 35.7657 | 35.2947 | 1.0133
279.6389 | 277.6612 | 300.3284 | 302.4505 | 277.5944 | 0.013542 | 0.017007 | OC | 30 | 44.8725 | -112582.739 | 279.6389 | 277.6612 | 0.0032208 | 0.0032088 | 1.4244e-05 | 1.7855e-05 | 0.070611 | 270.6654 | -0.014306 | -0.018456 | 0.0058725 | 0.0049928 | -3.9343e-06 | 2.1034e-06 | -0.0001634 | 0.2404% | 0.1574% | 2.5089 | 112.5827 | 30 | 277.6612 | 300.3284 | 112.5827 | 12674.8731 | 31259.8621 | 33811.7925 | 44.8725 | 43.8798 | 1.0226
279.3856 | 277.6435 | 294.2396 | 296.1137 | 277.5944 | 0.013545 | 0.017046 | OC | 30 | 36.7807 | -99206.7712 | 279.3856 | 277.6435 | 0.0035932 | 0.0038077 | 1.424e-05 | 1.7908e-05 | 0.057906 | 263.1722 | -0.015682 | -0.016799 | -0.01677 | -0.02073 | -1.3167e-06 | 2.8058e-06 | -0.00057334 | 0.2653% | 0.1574% | 2.6973 | 99.2068 | 30 | 277.6435 | 294.2396 | 99.2068 | 9841.9835 | 27544.118 | 29190.5567 | 36.7807 | 36.8266 | 0.99875
282.8115 | 277.9302 | 291.0756 | 295.802 | 277.0389 | 0.013568 | 0.016901 | OC | 30 | 58.7824 | -278127.1992 | 282.8115 | 277.9302 | 0.0032062 | 0.0031153 | 1.4265e-05 | 1.7767e-05 | 0.092635 | 412.4662 | 0.018821 | 0.016783 | -0.012612 | -0.0053719 | 2.2493e-06 | 1.5572e-06 | -0.00043287 | 0.1483% | 0.1576% | 4.7315 | 278.1272 | 30 | 277.9302 | 291.0756 | 278.1272 | 77354.7389 | 77299.9366 | 80956.0528 | 58.7824 | 55.1522 | 1.0658
279.5343 | 277.611 | 291.2667 | 293.28 | 277.5944 | 0.013551 | 0.016951 | OC | 30 | 35.5443 | -109568.755 | 279.5343 | 277.611 | 0.0031724 | 0.0034694 | 1.4255e-05 | 1.7806e-05 | 0.05643 | 271.1525 | -0.0079418 | -0.0083474 | 0.0060392 | 0.0060312 | -1.9967e-06 | 1.3366e-06 | -0.00062781 | 0.2475% | 0.1588% | 3.0826 | 109.5688 | 30 | 277.611 | 291.2667 | 109.5688 | 12005.3121 | 30417.4904 | 31913.726 | 35.5443 | 35.3573 | 1.0053
289.5277 | 284.8142 | 302.7595 | 307.6043 | 282.6005 | 0.013598 | 0.016853 | OC | 40 | 78.0202 | -268251.2897 | 289.5277 | 284.8142 | 0.0029348 | 0.0029898 | 1.4301e-05 | 1.7728e-05 | 0.12277 | 393.3409 | -0.0058587 | -0.004833 | -0.0019281 | -0.00031905 | -1.943e-06 | -2.9281e-06 | -0.00065074 | 0.1466% | 0.1574% | 3.4382 | 268.2513 | 40 | 284.8142 | 302.7595 | 268.2513 | 71958.7544 | 76401.7667 | 81215.6163 | 78.0202 | 70.2654 | 1.1104
286.2709 | 282.6626 | 303.1264 | 306.9824 | 282.5944 | 0.013569 | 0.016923 | OC | 40 | 66.2487 | -205180.5265 | 286.2709 | 282.6626 | 0.0029291 | 0.0030159 | 1.4276e-05 | 1.779e-05 | 0.10424 | 336.656 | 0.011004 | 0.0092159 | -0.00047354 | 0.0021235 | -2.1058e-06 | 9.242e-07 | 0.00082083 | 0.1641% | 0.1573% | 3.0971 | 205.1805 | 40 | 282.6626 | 303.1264 | 205.1805 | 42099.0485 | 57996.8562 | 62195.6415 | 66.2487 | 60.028 | 1.1036
285.4006 | 283.5238 | 303.1318 | 305.2244 | 283.15 | 0.013574 | 0.016975 | OC | 40 | 45.088 | -106773.5475 | 285.4006 | 283.5238 | 0.003368 | 0.0036187 | 1.4353e-05 | 1.7939e-05 | 0.072948 | 272.1195 | -0.023207 | -0.024732 | 0.0045252 | 0.0058863 | -2.1951e-06 | 1.9207e-06 | -0.00088374 | 0.2549% | 0.1618% | 2.3681 | 106.7735 | 40 | 283.5238 | 303.1318 | 106.7735 | 11400.5905 | 30272.8448 | 32366.4566 | 45.088 | 42.954 | 1.0497
286.9814 | 283.458 | 297.6877 | 301.4047 | 283.15 | 0.013586 | 0.016832 | OC | 40 | 54.6137 | -200538.2471 | 286.9814 | 283.458 | 0.0029655 | 0.003193 | 1.4298e-05 | 1.7678e-05 | 0.085884 | 333.415 | -0.034163 | -0.032516 | -0.0030111 | -0.0095429 | 3.4364e-07 | -9.3384e-07 | 0.00045772 | 0.1663% | 0.1573% | 3.6719 | 200.5382 | 40 | 283.458 | 297.6877 | 200.5382 | 40215.5885 | 56844.1699 | 59697.7753 | 54.6137 | 51.3705 | 1.0631
284.691 | 283.1457 | 297.4741 | 299.2214 | 283.15 | 0.013555 | 0.016877 | OC | 40 | 36.5395 | -87817.2559 | 284.691 | 283.1457 | 0.0034953 | 0.0040556 | 1.4268e-05 | 1.7729e-05 | 0.060164 | 270.028 | -0.0057716 | -0.0066773 | 0.0077199 | 0.0076934 | -1.0876e-06 | -2.5574e-06 | -0.00054372 | 0.3075% | 0.1647% | 2.4034 | 87.8173 | 40 | 283.1457 | 297.4741 | 87.8173 | 7711.8704 | 24865.0754 | 26123.3605 | 36.5395 | 35.7637 | 1.0217
286.6121 | 283.1362 | 291.9849 | 295.5484 | 283.15 | 0.013581 | 0.016876 | OC | 40 | 46.7515 | -197800.5322 | 286.6121 | 283.1362 | 0.0029442 | 0.003034 | 1.4271e-05 | 1.7731e-05 | 0.073519 | 330.455 | -0.0026947 | -0.0037755 | -0.0029856 | -0.0065589 | 7.6263e-07 | 1.506e-06 | -0.00096703 | 0.1671% | 0.1573% | 4.2309 | 197.8005 | 40 | 283.1362 | 291.9849 | 197.8005 | 39125.0506 | 56004.4916 | 57754.7727 | 46.7515 | 43.3999 | 1.0772
284.0932 | 280.7379 | 302.8783 | 306.5288 | 279.8167 | 0.013563 | 0.016974 | OC | 40 | 65.6464 | -190914.0394 | 284.0932 | 280.7379 | 0.0029823 | 0.0030648 | 1.4254e-05 | 1.7832e-05 | 0.10325 | 325.4226 | -0.024175 | -0.023221 | 0.00068429 | 0.0024457 | -1.9183e-06 | -1.6452e-06 | 0.00052843 | 0.1705% | 0.1573% | 2.9082 | 190.914 | 40 | 280.7379 | 302.8783 | 190.914 | 36448.1704 | 53596.8088 | 57823.7249 | 65.6464 | 58.0498 | 1.1309
284.4914 | 280.7979 | 297.5115 | 301.4411 | 279.8167 | 0.013587 | 0.016943 | OC | 40 | 58.1627 | -210487.6718 | 284.4914 | 280.7979 | 0.0031364 | 0.0038696 | 1.4276e-05 | 1.7808e-05 | 0.091509 | 342.9693 | -0.041172 | -0.036511 | -0.0064166 | -0.016688 | -5.0641e-08 | -2.6448e-06 | 0.00092785 | 0.1629% | 0.1573% | 3.6189 | 210.4877 | 40 | 280.7979 | 297.5115 | 210.4877 | 44305.06 | 59104.5013 | 62622.5111 | 58.1627 | 53.9493 | 1.0781
282.0807 | 280.4472 | 297.4814 | 299.3455 | 280.3722 | 0.013562 | 0.016971 | OC | 40 | 38.4913 | -92996.5628 | 282.0807 | 280.4472 | 0.0029854 | 0.0031358 | 1.4192e-05 | 1.7741e-05 | 0.060472 | 258.0569 | -0.0010028 | -0.0013455 | 0.0037709 | 0.0038253 | -4.5915e-06 | 4.4778e-07 | -1.2022e-05 | 0.2775% | 0.1571% | 2.416 | 92.9966 | 40 | 280.4472 | 297.4814 | 92.9966 | 8648.3607 | 26080.6277 | 27664.7478 | 38.4913 | 37.5604 | 1.0248
279.5588 | 277.5836 | 300.3383 | 302.4651 | 277.5944 | 0.013537 | 0.017018 | OC | 40 | 44.7598 | -112408.473 | 279.5588 | 277.5836 | 0.0029836 | 0.0030669 | 1.4157e-05 | 1.7779e-05 | 0.070177 | 268.405 | 0.0063339 | 0.0067296 | 0.0019141 | -0.00169 | 2.9536e-07 | -1.1499e-06 | 0.00068557 | 0.2388% | 0.1568% | 2.5114 | 112.4085 | 40 | 277.5836 | 300.3383 | 112.4085 | 12635.6648 | 31202.7458 | 33760.568 | 44.7598 | 43.8971 | 1.0197
281.3109 | 277.7153 | 294.9295 | 298.6486 | 277.0389 | 0.013563 | 0.016995 | OC | 40 | 53.577 | -204896.5795 | 281.3109 | 277.7153 | 0.0029353 | 0.0031045 | 1.4189e-05 | 1.776e-05 | 0.083815 | 334.8614 | -0.00956 | -0.011038 | 0.0015114 | -0.0025104 | -2.371e-06 | -1.4591e-06 | -0.00014703 | 0.1634% | 0.1564% | 3.8243 | 204.8966 | 40 | 277.7153 | 294.9295 | 204.8966 | 41982.6083 | 56902.9229 | 60430.0393 | 53.577 | 50.9971 | 1.0506